FISH PASSAGE O&M COORDINATION TEAM

Adult and Juvenile Fish Facilities Status Report

U.S. Army Corps of Engineers, Walla Walla District

July 9, 2009

Construction

McNary:
· All 14 turbine units are in service.
· Turbine unit 13 was out of service June 15 – 23 for external thrust bearing oil cooler pipe work.
Ice Harbor:

· Turbine unit 2 taken out of service for annual maintenance on June 23.  All 5 remaining turbine   units are in service.

Lower Monumental:

· All 6 turbine units are in service.
Little Goose:  
· All 6 turbine units are in service.
Lower Granite:
· All 6 turbine units are in service.

Operations and Maintenance - Juvenile Fish Facilities
Collection for fish transport continues at Lower Granite, Little Goose and Lower Monumental dams.  Every-other-day barge departures began June 1.  No date has been determined for the start of transport operations at McNary Dam.  
McNary: 

·   Primary and Secondary bypass operations on alternate days have been taking place since April 8.  Some secondary bypass is taking place outside of this schedule to accommodate USGS research.
·   VBSs: a total of 12 VBSs were cleaned on June 15 due to excessive debris accumulations.         

Ice Harbor:
·   Sampling is taking place on Tuesdays and Fridays.  The July 3 sample was cancelled to avoid exceeding wild juvenile Fall Chinook take limits.  Sampling resumed July 7 after modified take permit was received.
·   STSs are in continuous run mode.
Lower Monumental: 
·   STSs are in continuous run mode.

·   Primary dewaterer screen cleaner needed repairs on June 23.  The cable spreader sheave was replaced.

Little Goose:
·   A damaged VBS screen sections was discovered in gatewell slot 2A on June 10 and repaired June 18.  Because bulkheads still needed to be moved, turbine unit 2 was out of service until June 23.     

Operations and Maintenance - Adult Fish Facilities  

McNary:
· Adult lamprey video counts began July 1.  
· Fishway Entrance software successfully tested June 24.  The software will allow lowering of weirs at night for lamprey passage research.  
· North Oregon ladder AWS taken out of service May 28 following failure.  Bulkhead installed June 8 for planned inspection.  South AWS continues to provide sufficient water.    
· Fish Pumps: Pumps #1 & #2 are in service.  Fish Pump #3 is currently unwatered       

    and out of service for oil leak repairs.
Ice Harbor:

· North Shore Fish Pumps: Fish pumps #1 & #2 in service.  Fish Pump #3 is being repaired under warrantee.
·  South Shore Fish Pumps: all available for service. 
Lower Monumental:
· Fish Pumps 1 & 2 in service.  Fish Pump #3 remains out of service for diffuser assembly repairs and bearing housing replacement. 
Little Goose:
· NPE3: Although the bulkhead sealing off this entrance is evidently damaged, fishway performance does not appear to be adversely affected.  Criteria continues to be met.     
Lower Granite:

·  Fish pumps 1 and 3 in operation.  Fish pump 2 repairs are nearing completion. This pump has been out of service since the winter maintenance season for bearing replacement.  Maintenance personnel are to fabricate and install new seals before returning the pump to service.   
Other
Spill: Summer spill began at Snake River locations on June 21, and on June 20 at McNary Dam.
McNary:

· Cooling water strainers in turbine units 1-4, 6, and 8 – 14 inspected June 15 and 17.  Thirty juvenile lamprey mortalities and 1 live juvenile lamprey recovered.  Strainers in turbine units 5 and 7 could not be opened for inspections. 
·  Spillbays 16 – 22 (including spillbay weirs) were shut down for approximently 4 hours in support of hydro-acoustic antenna repairs and installation.  
Ice Harbor:

· RSW in operation.
· All cooling water strainers were cleaned the week of June 19 – 25.  A total of 8 lamprey mortalities were removed. 
Lower Monumental:

· RSWs is in operation.
Little Goose:

· TSW placed into operation (low crest configuration) April 3.  Taken out of service 1335 – 1746 hours on April 16 to adjust south side of gate slot (gap filler in stoplog/bulkhead slot). 
· Smolt Passage and Survival Study – study began April 16.
Lower Granite:

· Adult trap is in operation.
· RSW is in operation.

· NMFS transport research concluded June 12.
