
AGENDA

Fish Passage Operation and Maintenance (FPOM) Team meeting

May 9, 2013 (0900-1400)

CRITFC Celilo Room

Conference line: 888-675-2535
Accesss/Security code: 4849586  

1. Approve April 2013 FPOM minutes. (Mackey)
2. Action Items

2.1. NWW Action Items

2.2. NWP Action Items

2.2.1. [Feb 13] BON AFF PIT tag detector.  ACTION: Fryer will have detailed drawings, an operating plan, and monitoring plan for FPOM review in October.

2.2.2. [Apr 13] Hazing activities.  ACTION:  Include a hazing appendix to the FPP.  Include sea lion hazing guidelines and avian hazing guidelines.  
2.2.3. [Apr 13] BON VBS Task Group.  ACTION:  Fredricks and Hausmann will write up a change form to update the language for when screens will be re-installed.  

2.2.4. [Apr 13] FPOM meeting location.  ACTION: Wills will check availability of his office for the July FPOM.

2.3. Action Items completed or to be discussed later in the agenda.

2.3.1. [Mar 13] BPA updates.  ACTION: Need to develop MOCs for those outages that take the Projects out of criteria (TDA Unit 18 and MCN).  STATUS: completed for TDA.  See MOC 13TDA04 BPA RAS testing.
2.3.2. [Apr 13] LWG collection channel study.  .  ACTION: Trachtenbarg will work with Fone to develop a MOC for this study and operation.  STATUS: MOC sent out to FPOM members on April 17, with no objections received.  Approved.

2.3.3. [Apr 13] 13AppG002 IHR Updated Adult Trapping Operations.  ACTION:  Pinney will update the change form after the FPOM discussion and send it to Fone for formal FPOM concurrence. Updated in consultation with NOAA Fisheries and University of Idaho.  Final version sent out to FPOM members on April 26, with no comments received.  Approved. 

2.3.4.  [Apr 13] Bettin asked if MCN would be raking trash 8 – 11 July, so it coincides with the BPA RAS testing.  ACTION: Dugger will talk with MCN and Bettin to see if that can be accommodated.  STATUS: concurrent raking and RAS testing is not likely to happen.  The RAS testing requires unit outages for a different (perhaps shorter) periods of time than trash raking does.  The crane will not be available for both activities to occur concurrently.
2.3.5. [Apr 13] Kelt Video Counting.  ACTION: Klatte will check with FFU to see when the video monitoring stopped.  STATUS: Kelt video counting ended March 25 when the DVR was full, but they were only read through March 22 (we had already met CC open criteria.  The old camera and video system is and always has still been present and PSMFC can use that anytime.  We pulled our camera and DVR out as PSMFC stated they had no funds to review additional video and had no intent to use our system and John will be using much of the equipment this summer anyway.
2.3.6. [Mar 13] JMF and SMF condition sub-sampling data.  ACTION: Mackey will outline the data that will be lost by stopping sub-sampling information.  STATUS: discussed later in the agenda.
2.3.7. [Apr 13] Sturgeon Task Group.  ACTION: The task group will write up the change form and submit at the May FPOM.  STATUS: to be discussed later in the agenda.
3. Updates 

3.1. NWW Updates

3.1.1. LMN hydrocannon repaired on April 18

3.1.2. Trash at MCN- will need to coordinate a debris spill prior to removing TSW’s

3.1.3. LGR ADCP without spill- 

3.2. NWP Updates

3.2.1. BON A-Branch/ FV3-7 leak investigation.  
3.2.2. BON Updated Dewatering Plans.  
3.2.3. BON unit 8 RTS testing needs.
3.2.4. TDA spillbays.  Bay 9 v Bays 10/11.  
3.3. Research/FFDRWG updates.  Approval letters, permits, etc located at  www.nwd-wc.usace.army.mil/tmt/documents/FPOM/2010/NWP%20Research/Research.html
3.3.1. BON TRD.  
3.3.2. AFF modifications.  
3.4. RCC update.  
	Project
	Previous day average (kcfs)
	5 day forecast (kcfs)
	10 day forecast (kcfs)

	LWG
	
	
	

	MCN
	
	
	

	BON
	
	
	


3.5. Pinniped update.  

3.6. Lamprey updates.  

3.6.1. BON WS lamprey structure.  

3.6.2. BON CI LPS mods.  

3.6.3. JDA Lamprey collection protocols. Still working on the hoist; should be installed by the end of April.  No protocol in place yet, but FPOM would like to have an opportunity to look at the hoist in operation to help craft those protocols.  Still need to work out:  (1) All parties need to agree on time of day and frequency of operation.  It is anticipated the tribes will be operating the trap daily from July – August and maybe into September.  (2) Need to make sure that any and all operators of the jib crane/hoist are properly trained and that appropriate safety requirements are met.  (3) How and where should JDAS trap ops be included in the 2013 FPP? 

3.7. Avian.
3.7.1. NWW bird hazing update

3.7.2. Lethal take of gulls for tern management
3.8. BPA updates.  
3.9. Critical Spare parts lists.  (Takabayashi)  Bushing bearing and spare transformer study update.

4. BON JMF separator bar monitoring contract.  (Mackey)
4.1. Condition sub-sampling v regular SMP index sampling.
5. Coordination/Notification forms (need concurrence).  

5.1. 13TDA04 BPA RAS testing.
5.2. 13MCN06 Oregon shore adult fishway entrance weirs
5.3. 13IHR08 – 3D cam replacement and MU cooler inspection testing
5.4. 13LGS01A LGS spillway gate / stop log / diesel generator testing

5.5. 13LWG03 LWG powerhouse roof repair 

6. Fish Passage Plan:  Final 2013 FPP has been posted to the website:  http://www.nwd-wc.usace.army.mil/tmt/documents/fpp/2013/index.html.  
6.1. 2014 change forms.  
6.1.1. 14BON001 
6.1.2. 14TDA001 Wicket gate opening

6.1.3. 14JDA001 Wicket gate opening

6.1.4. 14LMN001 Unit 1 change in priority

7. Task Group Updates. 
7.1. BON unit operating range (Lorz).   Team members include Baus, Benner, Bettin, Chockley, Conder, Cooper, Fredricks, Hausmann, Hevlin, Lorz, Mackey, Meyer, Tackley, Rerecich, Wills. 

7.2. BON VBS task group.  (Hausmann).  Team members include Baus, Bettin, Fredricks, Hausmann, Lorz, Mackey, Rerecich, and Wills.  Fredricks said the main purpose it to better clarify the FPP criteria for re-installing screens and how to keep screens in throughout the year.  

7.2.1.  VBS backer screen required bus line clearance.  

7.2.2. Hausmann said he has taken a closer look at the reinstallation criteria.  In the field, the actually reinstallation was close to the recommended installation criteria.  

7.2.3. ACTION:  Fredricks and Hausmann will write up a change form to update the language for when screens will be re-installed.  Fredricks would like the final re-installation decision be left up to the Project.  This decision would be based on some data and professional judgment.  

7.3. Sturgeon task group (Van der Leeuw or HausmannACTION: The task group will write up the change form and submit at the May FPOM.  STATUS: Hausman reported “Bonneville doesn't allow wicket gates to be opened when tail logs are not in so we have no protocol to speak of other than that.”  Cordie and Zyndol submitted FPP change forms.
7.4. AFF mods (Rerecich).  

7.5. Fish counting task group (Setter).  Team members include Fredricks, Klatte, Mackey, Setter, Tackley, and Wills.  
8. Calendar items/ next FPOM agenda items.  (Check the CY13 on the website)

Memorandums of Coordination
☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺

Coordination Title: 13TDA04 BPA RAS testing

COORDINATION DATE- 16 Apr 2013

PROJECT- The Dalles Lock and Dam

RESPONSE DATE- 09 May 2013 (FPOM)
Description of the problem- Unit 18 is a fish priority unit due to its open sluicegates. BPA is requesting units 17-22 out of service for DC RAS testing on July 18 and July 22 for approximately 10 hours each.  Unit 16 will be the priority unit. Approximately 1 hour will be needed to close and open unit 16 chaingates each time.

Type of outage required- Unit 18 and associated sluicegates.  
Impact on facility operation- Change to unit 16 as priority operating unit with associated chaingates open.
Length of time for repairs- 10 hours each day
Expected impacts on fish passage- No impact is expected because all units east of unit 16 will be off line, hence no turbine entrainment. Unit 16 will have its chaingates open for sluiceway passage. 

Comments from agencies

Final results
☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺

COORDINATION TITLE -  13 MCN 06 North Entrance Weirs, McNary Dam Oregon Shore Fish Ladder

COORDINATION DATE -  6 May 2013

PROJECT -  McNary Lock and Dam

RESPONSE DATE -  9 May 2013
Description of the problem: The north entrance weirs on the Oregon Shore Fish Ladder (NFEW2 and NFEW3) have been increasingly out of calibration in recent weeks, probably due to partial failure of the metal wheels that guide the weirs in their slots.  The following shows the ladder check dates and associated problems:

5/1:  NFEW3 slack approx by 1 foot; NFEW2 OK

4/28:  NFEW2, slight slack - possibly out of criteria

4/26:  Slack not documented – different inspector

4/24:  NFEW2, much slack; NFEW3 OK

4/21:  NFEW2 slack; NFEW3 OK

4/19:  Slack not documented– different inspector

4/17:  NFEW2, much slack; NFEW3, light slack

4/14:  No slack noted.

4/12:  Slack not documented– different inspector

4/10:  No slack

4/8:  NFEW3 - some slack?

4/5:  Slack not documented– different inspector

4/3   NFEW2 and 3:  very light slack

3/31:  NFEW2 slack

3/29: No slack noted

3/21 to 3/28:  Slack not documented

3/17: NFEW:  Slight slack:  First time we noticed and documented it.

The Assistant Biologist started noticing problems on occasion since 3/17 and more frequently since April 17.

The slack condition of the cables has caused the following problems:

1. The weirs could jam in place, and at low tailwater we could have a worse passage problem;

2. During inspections, we have found slack in the cables that suspend the weirs.  

Right now, the ladder is probably out of criteria, and not by just a few inches.  When NFEW2 has slack it is 2 to 4 links slacked into the flow with the links being 6 to 8 inches long. This would be more than an inch or two out of criteria - more like about a foot or more.  On May 1 the LED dial read 8.5 feet but we estimated the weir to be at 7.5 feet based on the slack and links' length.  

3. The weirs are to be lowered at night for lamprey passage from 6/15/2013 to 9/30/2013.  If they continue to hang up, that defeats the purpose of the lowering.

With slack cables, there is no way to know accurately whether or not the weirs are in calibration, or how far they are out of calibration, as they are under swift water, so you can’t just drop a tape and measure them.  The problem only occurred in the past few weeks, which is why we didn’t do the job during the winter maintenance period.
Type of outage required:  The job takes time but the actual swap would be very short.  It will likely take less than 1 hour to replace each weir: 

The procedure:

1. Lowering Weir 1, in order to reduce back pressure;

2. Pull out one old weir;

3. Replacing it with a repaired weir that has the new UHMW rollers on it;

4. Raise Weir 1 again.

We can probably do this without shutting down the fish pumps, as entrance weirs are on rollers for the very reason that they are designed to operate against a pressure head.  They will move whether or not pressure is against them.  We need to do this twice:  Once for NFEW2, and once for NFEW3, probably a day or two later, as we need to put the new rollers on the pulled weir.  This means being out of criteria for up to two hours total, vs. being way out of criteria for days on end during a heavy fish run.  NFEW1 is normally held in a raised position and its replacement can wait until the winter maintenance season.

The project believes that this can be accomplished without a fish pump outage and without reducing the ladder flow.  However, we do want the authority to shut down one or both fish pumps if the flows are too strong against the problem weirs.  Potential adverse impacts to fish would be the removal and immediate replacement of each of the 2 weirs, plus reduced flows if we need to shut down one or both fish pumps for up to an hour per weir.  Impacts to fish could be reduced by starting the project as soon as crews and repair parts are available, and by conducting the work between 1400 and 1500, when diel charts show fish migration is at its lowest level of the daylight hours.
Impact on facility operation:  Minimal.  Studies by the University of Idaho indicate that the North Entrance only passes about 11% of the adult fish that enter the Oregon ladder.  The rest pass through the south entrance and the powerhouse floating weirs.  We would just be tying up a crane and crew for the operation.  Fish pumps would hopefully not be affected, and ladder flow would not be reduced, unless problems arise and we need to shut the pumps down for short periods.  On the positive side, we would know that the weirs would be operating within the criteria established by the Fish Passage Plan.  Each of the two replacements would only take about an hour apiece.

Dates of impacts/repairs:  We propose to start the work the first work day after approval is received.

Length of time for repairs:  About an hour per each of two weirs, not counting shore time to prepare the replacement weirs.  The first set of replacement weirs could be ready in a day; other replacement weirs would need to be prepared from the old weirs that are removed.  Both bulkheads could be replaced in three days, in two one-hour episodes.

Expected impacts on fish passage:  We would know that the weirs would be operating properly, at the proper depths.  We would also reduce or eliminate the need for emergency repairs later in the season while even larger numbers of fish are passing over the ladder.

Comments from agencies:

Final results:

☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺

COORDINATION TITLE- 13 IHR 08 3D cam replacement and MU cooler testing COORDINATION DATE-  April 25, 2013

PROJECT- Ice Harbor
RESPONSE DATE- FPOM – May 9, 2013

Description of the problem – The project is going to be taking out Main Unit #4 to replace the 3D cam blade transducer as well as perform Eddy Current heat exchanger testing on a main unit cooler.  The testing on the Main Unit Cooler is to support the work on the Lamprey improvement modifications on Main Unit #4.  All parts will be on-hand prior to taking this unit OOS for the 3D Cam transducer replacement on 5/13/13 and the unit will be returned to service on 5/15/13.

Type of outage required. – Main turbine unit 4 will be out of service during this time period.  This is a maintenance outage to perform repairs prior to spring runoff.

Impact on facility operation – Ice Harbor Main Unit Priority is currently 1, 3, 4, 2, 5, and 6.  Main Unit #4 will be out of service for this repair and will be tested out of priority when the repair is complete per section 4.3.2 of the FPP.  Main unit 2 will be operated as next in priority.

Dates of impacts/repairs –- 5/13/2013-5/15/2013



Length of time for repairs – 5/13/2013-5/15/2013
Expected impacts on fish passage – Adult migrating spring Chinook run could be peaking during this period.   No expected impact on fish passage.  Both adult fish ladders will remain operational.  Powerhouse hydraulic capacity is not expected to be exceeded forcing additional spill and higher dissolved gases.  Main turbine units 1, 2, 3, and 6 (if unit 5 remains out of service due to blade cracking) operating hydraulic capacity total approximately 56K plus fish spill at either 45 K or 30% of river flow.  See graphs below.

 [image: image1.png]Inflow (efs)

STP Extended Forecast
SNAKE-ICE HARBOR DAM (IHDW1)
Forecast Period 0423 to 0820

220000
200000 ¢ ~ Ohservation
— Current Foresast
e ¥ Previous Forecast
180000 . 90 Clinatology
502 Clinatology
v 107 Clinatolos
160000 2
140000 o
120000 -
100000
80000
60000
40000
20000 .
o
APR maY N o AuG sep

Month





[image: image2.png]#Fish

000

8000

7000

6000

5000

4000

3000

2000

1000

Predicted Adult Spring Chinook Arrival Peak and Run Size at Bonneville Dam
Peak Arival and Run Size Prediction on 4/23/2013
Peak Arival Day: 4/28/2013 (118) Run Size: 89021 StDev: 5.33333333333333

03/23 04/08 04/20 05/04 05/18 08/01 08/15

Daily Observed Adult Counts  * Predicted Peak Arival (Preseason)
Predicted Peak Amival (All Previous) —— Current Predicted Peak Arrival ——




[image: image3.png]2012, lee Harbor, Chinook, 10YrAvg 2012-2003

8000

7000 120

6000 100

5000 g
0 o

4000 2

£

o &

3000 3
w0 =

2000

1000 20

0 0

01/01 02/01 03/01 04/01 05/01 06/01 07/01 08/01

Adult Passage (124685) ——
Adult Chin 10YrAvg (100884) ——
Adult Chin Jek 10YrAva (27515) ———

09/01 10/01 17/01 1201

Adult Stihd 10YrAvg (182774) ——
Adlt Stihd-W 10YrAvg (44072) ——
Inflow 10Yr Ava





Comments from agencies

From: Trevor Conder - NOAA Federal [mailto:trevor.conder@noaa.gov] 
Sent: Tuesday, April 30, 2013 8:08 AM
To: Moody, Gregory P NWW
Cc: Bill Hevlin - NOAA Federal
Subject: Re: FPOM: IHR 3D cam replacement (UNCLASSIFIED)

Greg, 

I don't see any problem with this request prior to the FPOM discussion. Seems best to get this fixed before the spring runoff as suggested. 

-Trevor

Final results

☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺

COORDINATION TITLE – 13-LGS 01A Spillway Gate and Stop Log Testing

COORDINATION DATE-   May 2, 2013


PROJECT- Little Goose Lock and Dam


RESPONSE DATE-  09 May 2013 (May FPOM Meeting) 
Description of the problem:
  The Little Goose Periodic Inspection for Dam Safety requires the spillway gates to be operated by the spillway diesel generator. The scheduled date for this test was missed on March 28th. The Dam Safety program requires that this test be performed within 90 days of the report being written. A make-up test must be scheduled inside the spill season.

Little Goose Project has two contracts requiring Spillway Stop log activities for completion of these contracts, the first is the replacement of the Intake Gantry crane requiring functional commissioning of the Crane capabilities. This requires taking one spillway gate out of service to place and then remove the spillway stop logs. The second contract was the purchase of new spillway stop logs, the commissioning also requires taking one spillway gate out of service and testing functionality and fit.  Some FPOM discussions have taken place under a previous Coordination Request where final action has not yet been taken (for details see 13 LGS 01 Spillway Stop Log Testing).     

Type of outage required:   An operational change is being requested for (2) one-day periods at a time.

During peak seasonal flow of the Snake River, when spillway bays are passing water, a differential movement of gates is being requested. The spillway diesel generator will move one gate up and the adjacent gate down. Then after 5 minutes return both gates to their appropriate position. The process will be repeated until all gates have moved up and down a single stop once for the Dam Safety program.  This operation should take 1 hour or less.

During the commissioning activities for the Crane and stop log testing a one day outage of one spillway Bay to place and remove stop logs.  However, testing may extend into a second day, which is why an outage of 2 separate days is being requested.

Impact on facility operation:   Transferring power to the diesel generator will be the biggest impact to the facility. Operating the navigation lock during this time will not be recommended. This outage is only expected to be 1 hour or less. Timing the test for when no boats are coming would mitigate this issue. Differential adjustment of the spillway gates will not impact the total water passing through the spillway during the Dam Safety inspection activities.

During the commissioning activities for the Crane and stop log testing a one day outage of one spillway bay to place and remove stop logs will be required.  Since the total flow through the project is projected to be less than 80kcfs one or more spillway bays would not be used to match the required spill pattern, therefore the test would not impact spillway functionality for the published FPP spill pattern.

Length of time for repairs:  Two full days is the estimate to complete the work, the requested time frame would need to occur during the week of June 17-21, daily outages only, spillway bays would be returned to normal operations at the end of each day. The requested time frame would give the project the needed flexibility to conduct these operations and allow for unplanned slippages or problems encountered during the testing.

Expected impacts on fish passage: Little to no impact on fish passage is expected.

Expected total Snake River river flows in the June 17 – 21 timeframe is approximately 47 –  54 kcfs.  In low crest TSW configuration, the FPP spill pattern calls for TSW operation with 1 or 2 stops in spillbays 2 and 8.  In high crest TSW configuration, 1 to 5 total stops would be needed.  Under these conditions non-TSW bay configuration would range from 1 stop each in bays 1 and 8; to 1 stop each in bays 2, 4 and 6 plus 2 stops in bay 8 (with 2 unit operation and 31% spill).  Given these conditions, transferring 1 or 2 stops to an adjacent bay, if necessary, produces very little effect on fish passage since TSW operation dominates tailrace conditions.

As can be seen on the charts below, The planned June 17 – 21 timeframe is after the peak of the spring Chinook run, prior to steelhead run arrival in late August and  just before the majority sockeye salmon begin to arrive.  Adult impacts can be minimized by conducting work between 1000 and 1700 hours when adult fish are the least active. 

[image: image4.jpg]Chinook Adult Passage at Little Goose Dam

Number of

04/12 04123 05104 0S/15 05126 0606 06/17 06128 07/09 07720 07131 08/ 1 08722 0SIT2 03113 09124 10105 1016 10727
Passage Date

Ten Vear Average (2003.2012)

2012

2015

Graph designed by the Fish Passage Center - Copyright © 2013 Fish Passage Center. Alrights reserved.
Graph design last updated on 03/13/13




  

[image: image5.jpg]Steelhead Passage at Little Goose Dam

04101 04712 04723 0SID4 0S/15 05126 06106 0G/17 08128 07709 07120 07731 0B/11 08122 0912 0913 09124 10105 10116 10727
Passage Date

Ten Vear Average (2003.2012)

2012

2015

Graph designed by the Fish Passage Center - Copyright © 2013 Fish Passage Center. Alrights reserved.
Graph design last updated on 03/13/13




[image: image6.jpg]Sockeye Passage at Little Goose Dam

Number of

0412 0423 05104 0S/15 05026 06106 06/17 0628 07/09 07720 07731 08/ 022 0912 09/13 03124 1005 1016 10227
Passage Date

Ten Vear Average (2003.2012)

2012

2015

Graph designed by the Fish Passage Center - Copyright © 2013 Fish Passage Center. Alrights reserved.
Graph design last updated on 03/13/13





Diel Adult Fish Passage at Little Goose:  2005 – 2010 diel adult passage date indicate that peak count hours for Spring Chinook, Summer Steelhead and Sockey are from 0700 to 1000 hours.  Scheduling tests after 1000 hours will minimize adult passage impacts yet allow crane worjk to take place in daylight conditions.  Night time tests would create additional safety hazards to the crane and rigging crew and impact night time juvenile fish passage over the TSW and spillway.  See charts below for additional hourly adult passage details. 
[image: image7.emf]
[image: image8.emf]
[image: image9.emf]
Comments from agencies

Final results:

☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺☺

COORDINATION TITLE- 13LWG03 Powerhouse Roof Repair
COORDINATION DATE- March 26, 2013 / May 6, 2013
PROJECT- Lower Granite Lock and Dam
RESPONSE DATE- March 29, 2013 / May 9, 2013
Description of the problem- See the Final Results section near the end of this document for powerhouse outage schedule changes.
Issues with the Existing Powerhouse Roof:  The existing roof on the Lower Granite powerhouse consists of polyurethane foam insulation (PUF) that was spray-applied directly to the corrugated structural steel roof deck.  It was installed in 1995 as rehabilitation to the original powerhouse roof which was also a PUF system.  The foam insulation is waterproofed with a two-coat application of spray-applied polyurethane roofing membrane.

The current roofing system has been exhibiting widespread blistering of the waterproof polyurethane membrane for several years and, thus, has been the subject of concern for water intrusion into the foam insulation.  Roof leakage has also been reported by Lower Granite Project personnel up to 20 feet from the roof perimeter, primarily along the downstream parapet wall of the powerhouse.   A roof moisture survey was conducted by an independent firm to determine the extent of water penetration into foam insulation and its potential to cause roofing system failure.  Due to limited funding, the survey was conducted only on the Erection Bay, which is the area of the powerhouse roof where the worst membrane blistering has occurred.  Here, the moisture survey identified varied but limited amounts of moisture within the foam insulation.  The moisture detected is primarily located in the top portion of the foam, which is generally an indicator of deterioration of the waterproof coating.  As noted in the moisture survey report, the coating problems appear to be the result of “age, normal deterioration, pin-holing, punctures and de-lamination of the coating from the foam insulation.”

The moisture survey report notes that the concentration of moisture found in the upper areas of the foam insulation ranges from a low of slightly above the ambient (or background) moisture level to a moderate moisture content which is still far below a moisture saturation level and levels of moisture which become visible to the human eye.

The moisture survey report notes that moisture intrusion into the foam insulation, when combined with the current age and limited visible deterioration of the waterproof polyurethane roofing membrane, clearly indicates that the roof system is need of maintenance and repair.  The polyurethane coating used on the powerhouse roof has a warrantable life expectancy of up to 10 years.  The coating is now going on 17 years in service and, thus, is due for replacement.  The moisture survey report also notes that, even though PUF insulation has a closed-cell structure that will resist moisture intrusion to some extent, once moisture enters this type of insulation, an accelerated cycle of roofing system deterioration begins.  Furthermore, although the current condition of the roofing system does not present a crisis situation, a plan of action with the goal of accomplishing repairs and rehabilitations within one to two years should nevertheless be put in place as soon as possible.  Any delay to making final repairs beyond two years will result in a significant deterioration of the current roofing system and, therein, significantly increase costs associated with its repairs.
Access to the powerhouse roof is required for the roof repair project.  Work includes a new moisture survey, removal and replacement of existing  roof insulation and membrane that is wet, scoured and otherwise damaged, installation of new PUF insulation, spray application of a new base and top coat for the roofing membrane (applied in four separate spray coatings in order to obtain the membrane manufacturer’s 20 year warranty), sealing open monolith joints in the vertical walls on the upstream and downstream sides of the powerhouse, and installing new hand rails along the downstream parapet wall of the powerhouse roof in order to facilitate safe worker access for roof maintenance and repair.

Issues with Accessing the Powerhouse Roof Under the Existing Electrical Bus:  The 500kV bus located on 5 of the powerhouse bays is approximately 23 feet from the roof.

Approach distances are specified in NFPA 70 E, Table 130.4(C)(a) and Table 130.4(C)(b) and the corresponding voltages to which the qualified person will be exposed. The 19ft figure that was determined to be the safe working distance was and is less restrictive than the OSHA criteria.  However the limitations for the use of this as a safe working distance doesn't apply to "unqualified persons" in this case and is only a recommendation from a consensus standard and not a regulation.

OSHA 1910.333(c)(3) states in its entirety;

“1910.333(c)(3)

"Overhead lines." if work is to be performed near overhead lines, the lines shall be deenergized and grounded, or other protective measures shall be provided before work is started. If the lines are to be deenergized, arrangements shall be made with the person or organization that operates or controls the electric circuits involved to deenergize and ground them. If protective measures, such as guarding, isolating, or insulating, are provided, these precautions shall prevent employees from contacting such lines directly with any part of their body or indirectly through conductive materials, tools, or equipment.

Note: The work practices used by qualified persons installing insulating devices on overhead power transmission or distribution lines are covered by 1910.269 of this Part, not by 1910.332 through 1910.335 of this Part. Under paragraph (c)(2) of this section, unqualified persons are prohibited from performing this type of work.

1910.333(c)(3)(i)

"Unqualified persons."

1910.333(c)(3)(i)(A)

When an unqualified person is working in an elevated position near overhead lines, the location shall be such that the person and the longest conductive object he or she may contact cannot come closer to any unguarded, energized overhead line than the following distances:

1910.333(c)(3)(i)(A)(1)

For voltages to ground 50kV or below - 10 feet (305 cm);

1910.333(c)(3)(i)(A)(2)

For voltages to ground over 50kV - 10 feet (305 cm) plus 4 inches (10 cm) for every 10kV over 50kV.”

The calculation of this safe work distance as referenced above is 25ft and is restated in EM 385-1-1, Section 11.F.04. and Table 11-1.

Bottom line is that working around energized overhead electric on the Lower Granite Powerhouse roof would be prohibited.

As for a waiver, it would not be allowed or granted due to 1910.333 being a Federal Statute and would violate federal law.  Any assumption of risk by District, Division or Headquarters would violate that and go against Risk Management regulations.

Lower Granite personnel looked into de-energizing a portion of the line, so work could be accomplished in phases.  They determined the entire line must be out.

Type of outage required- The contractor will work a 10-hour shift, from 1000 to 2000 hours, on July 15-16, 2013, to conduct the moisture survey.  The contractor will work a 10-hour shift, from 1000 to 2000 hours, seven days a week, from August 5 to September 19, 2013, to repair the roof.  It will take approximately 1.5 hours to do the safe clearance paperwork and hang clearance tags immediately preceding each day’s work shift and another 1.5 hours to do the paperwork and remove the tags immediately after each shift.  So a daily powerhouse outage from 0830 to 2130 hours is required to conduct this work.  All units will be out except for unit 5 (or unit 6 secondarily), which will run at speed- no-load for house power during the daily outage period.  Units will be available to operate from 2130 to 0830 hours. 

Doble testing is scheduled for August 12-16 and is already approved under Appendix A of the 2013 Fish Passage Plan (FPP).  For the doble testing, all units will be OOS from 0600-1800 hours typically, with units 5 and 6 in service from 1800-0600 hours.  The plant outage would extend until 2130 hours for the roof repair, and then only units 5 and 6 would be available the nights of Aug. 12-15.  Unit 5 and 6 operation for passing water and adult fish attraction would be shut off at 0600 hours or earlier for the doble testing. 

Impact on facility operation- The project may need to spill in September and spill additional water in August to pass water that is not used for generation because of the daily plant outages.  At typical river flows anticipated for that time, total dissolved gas levels are not expected to exceed the gas cap.

Commercial barge and fish barge navigation should not be affected by the anticipated spill levels.

There will not be any power disruptions to the adult and juvenile fish facilities, including the auxiliary water supply (AWS) pumps, adult fish trap, juvenile fish collection gallery, and PIT-tag detection systems.

Dates of impacts/repairs- The polyurethane foam and elastomeric urethane roofing membrane coating have strict application requirements for temperature and humidity.  These generally require the work take place during warm summer months with low probability of rainfall.

Contract Requirements:

“Do not apply sprayed polyurethane foam if the roof surface temperature is less than 50 degrees F, higher than 130 degrees F, or is less than 5 degrees F above the dew point.  Apply the elastomeric urethane roofing membrane coating over the foam insulation between the ambient temperature ranges of 50 and 100 degrees F.  Relative humidity shall be within limits recommended by the sprayed polyurethane foam manufacturer's and the elastomeric urethane coating manufacturer's printed instructions.”

Outage 1, New Moisture Survey:  15 July 2013 – 16 July 2013, 13 hours a day, 0830 – 2130, allows for contractor work 10 hours a day from 1000 – 2000

Outage 2, Roof Repair Work:  5 August 2013 – 19 September 2013, 13 hours a day, 0830 – 2130 pm, allows for contractor work 10 hours a day from 1000 – 2000

Length of time for repairs

Outage 1:  2 days

Outage 2:  6-1/2 weeks

Expected impacts on fish passage- With the powerhouse turbine unit outage from approximately 0830 to 2130 hours each day, excess water may be spilled, potentially putting more fish into the Lower Granite tailrace when water temperatures are up.

 Juvenile fish sample/collection numbers and fish transport numbers would be lower as a result of the daily plant outage.

 NOAA's late season fish transport study might be impacted for a week or so.

Turbine units will not be operating to provide adult fish attraction to the fish ladder from 0830 to 2130 hours each day.  However, units will be operating from 2130 to 0830 hours each day according to FPP priority.  The exception will be during the August 12-16 doble testing as mentioned above.  The fish ladder and AWS pumps will be operating to meet FPP criteria during the entire construction period.

As shown by the top graph below, adult fish passage counts at the Lower Granite count window are typically low in August and increase in September.  The lower two graphs show the average diurnal distribution of “B” run steelhead and fall chinook at Lower Granite, indicating that by 1000 hours the hourly counts are generally decreasing at the count window.  The turbine units will be operating till 0830 hours each morning to help attract adult fish to the ladder entrances, where the number of adults passing will probably be decreasing earlier than at the count window. 

[image: image10.png]Jak 10YrAvg/Adult Steelhead 10YrAvg/Adult Steelhead-Wild 10YrAvg/Adult
2012, Lower Granite, Chinook, 10YrAvg 2012-2003

k 10YrAvg/Adult Steelhead 10YrAvg/Adult Steelhead Wild 10YrAvg/Adult Cot

8000

7000

6000

5000

4000

3000

2000

1000

o

0101 0201 0301 04/01 05/01 0801 07/01 001 09/01 10/01 1101 12001

Adlt Passage (116619) —— Adult StIhd:W 10YrAvg (44336) —
Adult Chin 10YrAvg (89631) —— Adult Goho 10YrAvg (2779)
Adult Chin Jck 10YrAvg (29756) —— Adult Sock 10YrAvg (651) ——

‘Adult Stlhd 10YrAva (180185) —— Adult Shad 10YrAva (11226)




[image: image11.emf]
[image: image12.emf]
Comments from agencies

-----Original Message-----
From: Dave Benner [mailto:dbenner@fpc.org] 
Sent: Friday, March 29, 2013 12:41 PM
To: Fone, Kenneth R NWW
Subject: RE: FPOM: Lower Granite powerhouse roof repair (UNCLASSIFIED)

Ken-

A few questions:

1. The only survey so far has been conducted at the Erection Bay where the worst blistering has occurred.  Depending on what is discovered during the inspection on July 15-16, would it be possible to conduct 1/2 the work this year and 1/2 next year, starting in the most problematic areas. The coordination form states work should be accomplished in 1-2 years.  If work only extended through August, looking at adult steelhead and Chinook passage, it would avoid the September period when this outage would potentially have the largest impact on adult passage. 

2.  If work in September cannot be avoided, can work be accomplished at night- at least during the high adult passage periods. The coordination form does discuss the temperature requirements between 50-100 deg F.  I know during Sept nighttime lows do begin to drop off pretty quickly, just wondering if the nighttime option had been fully explored.

3.  If all work must be completed this year, extending into Sept and not at night: can the outage be delayed daily from 830-2130 to maybe 1000-2300, especially during period when adult numbers increase or have this happen if we begin to see an impact on daily passage.  Looking at your daily passage plots for LGR, having PH attraction for an extra 1.5 hrs in the morning would help. 

Thanks for the opportunity to comment.  Hope all is well.

Dave Benner

---------------------------------------------------------------------------------------

Other comments received were over the phone:

Tom Lorz (CRITFC) asked if the turbine units can be kept running until at least 0900 hours in the morning each day to provide attraction for adult salmonids to the fish ladder entrances.

Gary Fredricks (NOAA Fisheries) recommended that the spill pattern at Lower Granite be re-examined to ensure that there is flow loaded on the side bays for optimal attraction of adult salmonids to the fish ladders.  He asked if the turbine units can be kept running until 0900 or 1000 hours each day to provide attraction for adults to the ladder entrances.

Bill Hevlin (NOAA Fisheries) said that the current Lower Granite spill pattern in the Fish Passage Plan is a “crown” pattern to guide adults along the sides of the spill to the ladder entrances.  The adult fish daytime counts need to be monitored for the duration of the roof repair job.  If we find that adults are being delayed, perhaps one or two stops can be taken from the middle spill bays and added to the north bays.  He recommended that the turbine unit outage be delayed till 0900 or 1000 hours each day if possible.

Rick Kruger (ODFG) brought up the subject of this coordination form at the April 2 FPAC meeting.  Paul Wagner (NOAA Fisheries) said that the FPAC group recommended that turbine units be kept running until 0930 or 1000 hours each day, with 1000 hours being the optimal time.

-------------------------------------------------------------------------------------------

-----Original Message-----
From: Bill Hevlin - NOAA Federal [mailto:bill.hevlin@noaa.gov] 
Sent: Monday, April 08, 2013 11:17 AM
To: Fone, Kenneth R NWW
Cc: Bill Hevlin - NOAA Federal
Subject: Re: LGR powerhouse roof repair (UNCLASSIFIED)

Ken,

Thanks for the update. Operating turbine #2 for adult attraction until 9:30 every morning is okay with NOAA.  Please revise the MOC and send it to me, and I will reply.  Also, include that the COE will monitor adult counts before, during and after the altered operation period to estimate whether numbers of adults appear to be delaying downstream of Granite.  Also, as you said, include that during the dates of the double testing the operation will be changed. 

I'll be looking for your revised MOC.

thanks again Ken for the good coordination!

Bill Hevlin 

On Fri, Apr 5, 2013 at 1:31 PM, Fone, Kenneth R NWW <Kenneth.R.Fone@usace.army.mil> wrote:


Classification: UNCLASSIFIED


Caveats: NONE


Bill,


The feedback I received from FPOM folks for the start time of the daily LGR powerhouse unit outages ranged from 0900 to 1000 hours, with 1000 hours being the optimum time, but with 0930 or 0900 being acceptable to most folks.  The PDT for the Lower Granite powerhouse roof repair project will be putting into the contract that the hours available for the roofing work will from 1100 to 2130 hours each day, so the actual powerhouse unit outage will be from 0930 to 2300 hours.  As mentioned in the MOC, the doble testing at LGR will be occurring Aug. 12-16, starting at 0600 hours each day.  This extends the outage from 0600 to 2300 hours on Aug. 12-16.  The doble testing and 0600 start of the testing is in Appendix A of the FPP.


I'll be updating the MOC with the comments I received and the final results, which I'll also summarize at the FPOM meeting as an update.


Thanks,


Ken

Final results

Comments received were discussed with the Lower Granite roof repair PDT and taken into consideration to finalize the turbine unit outage schedule and daily work window for the contractor.  The unit outage schedule will be as follows:

OUTAGE 1: Moisture survey, 15 July 2013 and 16 July 2013 (2 days), 0930 - 2300 hours

OUTAGE 2: Roof repair work:

10 August 2013 - 11 August 2013, 0930 to 2300 hours 

12 August 2013 at 0600 hours to 16 August 2013 at 2300 hours, 24 hours per day between those dates (0600 to 1800 hours already approved for doble testing)

17 August 2013 - 22 September 2013, 0930 to 2300 hours

Lower Granite Project received notification from BPA on 2 May 2013, about a line outage conflict at the substation the week of 3-9 August 2013.  BPA needs the Lower Granite line available that week to keep the substation operable while they perform spacer replacement on another line.  The scheduled start and end dates for the roof repair will need to occur 5 days later.  To mitigate for that, the PDT is proposing a 24-hour per day outage during the August 12-16 period, which would move up the completion date from August 24 to August 22.   
When the powerhouse is in operation, turbine units will follow Fish Passage Plan operating priority. 

The work shift available to the contractor will be 10.5 hours long (includes 0.5 hour lunch break) during the 1100 to 2130 hours time frame, with the remainder of the time needed to prepare and place the safe clearance tags and remove the tags each day.  Project personnel have determined that the line feed for station service will need to be switched twice each day, at the start and end of the daily powerhouse unit outage.  This will result in the AWS pumps being out of service for approximately 5 minutes at 0930 hours and again at 2300 hours.

For the duration of the roof repair dates, adult salmonid numbers passing the count window will be monitored.  If the data indicates that adult fish passage is being delayed, in-season coordination will occur with the regional agencies to change the spill pattern to help with adult fish attraction to the ladder entrances.

Lower Granite project will coordinate with RCC and BPA on water storage operations in the Lower Granite pool that may be needed to reduce the extra water that would otherwise be spilled during the powerhouse outage, with the goal of keeping dissolved gas levels below the gas cap.    
Thank you,

Ken Fone

509-527-7140
FPP Change Forms
☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻

☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻

Change Request Number: 14TDA001 10 minute wicket gate test opening

Date:  04/30/2013

Proposed by: Bob Cordie 
Location of Change:  The Dalles Dam 

Proposed Change/Add: 

5.8. Turbine Unit Operation and Maintenance

Wicket gate opening for functional testing on a watered up unit will be no more than 10 minutes total open time.

Reason for Change: During turbine maintenance, the wicket gates require functional testing to put the unit back in service. We restricted this to 5 minute open time in the past to prevent sturgeon in the draft tube from entering the scroll case. This was a result of a history of sturgeon entering the scroll case when wickets were left open.

With the new digital governors on units, the wicket functional testing requires a few more minutes. Therefore we propose a 10 minute total open time. There is no data suggesting a hard limit to the amount of time wickets can be opened. Five minutes was selected as a project SOP to meet both maintenance and fish needs. The intent was to assure they weren’t left open for hours or days. Ten minutes is expected to give the same results. 

This is a project specific requirement and will likely not apply at other projects with differing sturgeon challenges.

Comments from others: 

Record of Final Action: 
☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻
Change Request Number: 14JDA001 15 minute wicket gate test opening

Date:  04/30/2013

Proposed by: Miro Zyndol 
Location of Change:  John Day Dam 

Proposed Change/Add: 

5.4. Turbine Unit Operation and Maintenance

Wicket gate opening for functional testing on a watered up unit will be no more than 15 minutes total open time.

Reason for Change:  Consistency with TDA.  During turbine maintenance, the wicket gates require functional testing to put the unit back in service. We restricted this to 5 minute open time in the past to prevent sturgeon in the draft tube from entering the scroll case. This was a result of a history of sturgeon entering the scroll case when wickets were left open.

With the new digital governors on units, the wicket functional testing requires a few more minutes. Therefore we propose a 15 minute total open time. There is no data suggesting a hard limit to the amount of time wickets can be opened. Five minutes was selected as a project SOP to meet both maintenance and fish needs. The intent was to assure they weren’t left open for hours or days.  15 minutes is expected to give the same results. 

This is a project specific requirement and will likely not apply at other projects with differing sturgeon challenges.

Comments from others: 
Record of Final Action: 
☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻

Change Request Number & Title: 14LMN001 – Unit 1 Priority Change
Date Submitted: May 6, 2013 

Project: Lower Monumental Dam

Requester Name, Agency: Brian Vorheis, Chief of Maintenance, Lower Monumental Dam

Location of Change - FPP Project and Section:

FPP13 LMN 4.1.  The change would be effective immediately.

  Proposed Changes (in track changes to existing section):

4.  Turbine Unit Operation and Maintenance

4.1.  Turbine Unit Operation.

When in operation, turbine units will be operated to enhance adult and juvenile fish passage from March 1 through November 30.  During this time period turbine units will be operated as needed to meet generation requirements in the priority order shown in Table LMN-5.  Unit operating priority may be coordinated differently to allow for fish research, construction, or project maintenance activities. If a turbine unit is taken out of service for maintenance or repair, the next unit on the priority list shall be operated.  Flows listed in Table LMN-5 are based upon daily average flows.  Also see Section 2.1, Spill Management.

Turbine Unit 1 was the Fish Priority unit prior to the failure of blade linkages.  Temporary repairs included blades being welded in fixed positions.  Operating turbine unit 1 improves juvenile fish passage by eliminating the eddy at the fish loading dock.  Turbine unit 1 operation is also preferred as operation attracts adult fish to the North fish ladder. Since this turbine unit has fixed blades and a narrow operation window, starts and stops can cause excessive wear and tear.  Unit 1 run priority is last on, first off for all flow conditions until blade link pin repairs are completed in 2015 or 2016.  Turbine unit 1 may be turned off at the power plant operator’s discretion, when the flows are between 55kcfs-70kcfs.

Table LMN-4.  Turbine Unit Operating Priority for Lower Monumental Dam.

	Season
	River Flow
	Spill Rate
	Unit Priority

	Fish Passage Season

March 1 – November 30
	
	
	

	
	
	
	

	
	Any River Flow
	Any Spill Level, including No Spill
	2, 3, 4, 5, 6 then 1**

	December 1 – end of February
	Any River Flow
	Any Spill Level, including No Spill
	Any Order


.  

** If no spill is occurring, U1 may be operated at any priority level at the discretion of project personnel.  NOTE:  U1 has fixed-pitch blades and can operate only at about 130 megawatts.  This unit priority sequence will remain in effect until unit 1 blade link pin repairs are completed in 2015 or 2016.
Justification for Change:
Main Unit 1 has fixed turbine blades due to the failed BLH link pins. With the blades not being able to rotate the blade seals are not exercised so after prolonged sitting in one position coupled with the pressure created on the blades from the water when the unit is running increases the probability of leaking oil from the blade seals. This probability is minimized when the unit is not run due to the removal of the water pressure from the blades. The unit is scheduled to be repaired in 2015.

Based on expected flows this would impact unit 1 being the priority run unit from 7 to 25 May 2013 and 31 May to 15 June 2013. Unit 1 will only run 5 days instead of 40 days based on expected flows.

Unit One is the preferred fish attraction flow unit, however, the potential for oil in the river is minimized under this change and a reduced potential for this problem justifies this change until repairs to unit one can be accomplished.  Unit 2 has served as the preferred attraction flow for the past few years and no passage problems have been detected.

Comments from others:

MOC 13LMN02  (Unit 1 Priority Change) was approved at the April FPOM meeting.  This change form is needed so the change will show up in the printed 2014 FPP in LMN Section 4.1

Record of Final Action:

☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻☻












16
1

