
FPP Change Request Form
Change Request Number: 14TDA005 Project Facts and Figures
Date Submitted:  8/8/2013
Project: TDA
Requester Name, Agency: NWP Fisheries
Location of Change - FPP Project and Section:

Backside of project tab (new section).
Proposed Changes:
Add new section:
Project Facts, Figures and Operating Criteria – The Dalles Dam, Columbia River (RM 191.5)

Reservoir

Lake Celilo (23.6 miles long)
Forebay Elevation

Minimum pool: 155.0 ft

Full pool: 160.0 ft
Tailrace Elevation 

Maximum rate of change: 3 ft per hour
Discharge Limits
Minimum (Dec-Feb): 12.5 kcfs

Minimum (Mar-Nov): 50 kcfs

Maximum rate of change: 150 kcfs per hour

Powerhouse 
Length: 2,089 ft

Turbine units: 22
Fishway units: 2

Station service units: 2

Total generating capacity (nameplate): 2,099 MW

Hydraulic capacity: 375 kcfs

Spillway

Length: 1,447 ft

Spillbays: 23
Navigation Lock

Chamber: 650 ft long x 86 ft wide, max lift 90 ft

Average transit time: 30 minutes

Justification for Change:
This information is often asked for but not readily found in the FPP.
Comments from others: 
Record of Final Action:

