Fish Passage Plan (FPP) Change Request Form

Change Form # & Title: 
15LGS001 – Unit 5 Restricted Operation 
Date Submitted: 

July 10, 2014
Project: 


Little Goose Lock & Dam
Requester Name, Agency: 
Lisa Wright, Corps RCC
Final Action:



FPP Section:
LGS Section 4 (Turbine Unit O&M) – Table LGS-7
Justification:
Little Goose Unit 5 is restricted to operate in the upper 1% range (~16–19 kcfs) due to vibration issues.  February 2012 HDC report documented vibration concerns with Unit 5 at loading below 120 MW.  Project SOP was issued in March 2012 to start Unit 5 as quickly as possible and bring to a base point of 130 MW or higher to minimize excessive vibration at points below 120 MW and prevent damage to the unit. 

Proposed Change:
Add footnote b to Table LGS-7 regarding Unit 5 operation.
Table LGS-7.  Little Goose Dam Turbine Units 4, 5, 6 Power (MW) & Flow (cfs) at Upper and Lower Limits of the ±1% Peak Efficiency Operating Range. a, b
(no changes to table – added footnote is the only change)
a. Table based on the 2003 index test of U4 and the 1975 turbine model test.

b. Unit 5 restricted to operate in upper 1% range (approximately 16.2–19.2 kcfs) due to vibration issues below 120 MW (HDC Report 2/22/12).  March 2012 SOP issued to start Unit 5 as quickly as possible and bring to base point of ≥ 130 MW to minimize excessive vibration at points below 120 MW and prevent damage to the unit.
Comments:
 
Record of Final Action:

15LGS001 - Page 1 of 1

