PP Change Request Form
Change Request Number: 14BON001 Table BON-16 Add PH2 Mid-Range
Date Submitted:  3/29/2013
Project: BON
Requester Name, Agency: FPOM BON Ops Task Group
Location of Change - FPP Project and Section:
BON section 5.2 (Turbine Unit Operating Range) and Table BON-16 (PH2 1% range)
Existing Language in 2014 FPP:

5.2. Turbine Unit Operating Range. 
5.2.1. Turbines will be operated within ±1% of peak turbine efficiency (1% range) from April 1 through October 31, as specified in the BPA Load Shaping Guidelines (Appendix C).
5.2.2. Turbine units at PH1 will operate within the 1% range and within cavitation limits at various project heads as shown in Table BON-15.
5.2.3. Turbine units at PH2 will operate at the mid to lower 1% range (unless total dissolved gas waivers are exceeded in the tailrace) and within cavitation limits at various project heads as shown in Table BON-16.
Proposed Language:

5.2.1. Turbines will be operated within ±1% of peak turbine efficiency (1% range) from April 1 through October 31, as specified in the BPA Load Shaping Guidelines (Appendix C), and as defined in Tables BON-15 (PH1) and BON-16 (PH2).  Through regional coordination with FPOM and TMT, the 1% operating range guidelines have been modified to minimize turbulence in PH2 gatewells for bypassed juvenile salmonids until structural and/or other solutions are implemented.  The modified turbine unit operating ranges are defined below in section 5.2.2.  
5.2.2. From April 1 through October 31
, turbine units will operate sequentially in the following order of operating ranges to pass increasing levels of flow:

a. PH2 units within 1% mid-range; 

b. Then, PH1 units up to 1% upper limit;

c. Then, PH1 units up to BOP;

d. Then, additional flow in excess of what can be passed in steps above will be passed in one of the three following ways:

i. April 1–April 9: PH2 units up to 1% upper limit.  

ii. April 10–June 15 (Spring Spill) w/ Juvenile
 Trigger
: When
 juvenile spring Chinook collection counts at BON JMF are greater than adult spring Chinook total passage counts for three consecutive days (juvenile trigger), Project Fisheries will notify the control room to maintain PH2 units within 1% mid-range as a hard constraint and pass additional flow as spill.  
iii. April 10–June 15 (Spring Spill) w/ Adult Trigger
: When adult spring Chinook (excluding jacks) total passage counts are greater than juvenile spring Chinook collection counts at BON JMF for two consecutive days (adult trigger), Project Fisheries will notify the control room to operate PH2 up to 1% upper limit in priority order from north to south: 18, 17, 16, 15, 14, 13, 12, 11. 
iv. June 16–October 31: PH2 units up to 1% upper limit.  

Table BON-1.  Bonneville Dam Powerhouse Two Turbine Units 11–18 Output (MW) and Discharge (cfs) Per Unit at Lower, Mid-Range and Upper Limits of the 1% Peak Efficiency Operating Range.1
	 
	Powerhouse Two (Units 11-18)

	 
	With STS
	No STS

	Project 
	1% Lower Limit
	1% Mid-Range
	1% Upper Limit
	1% Lower Limit
	1% Mid-Range
	1% Upper Limit

	Head
	
	13kcfs
	15kcfs
	
	
	13kcfs
	15kcfs
	

	(ft)
	(MW)
	(cfs)
	(MW)
	(MW)
	(MW)
	(cfs)
	(MW)
	(cfs)
	(MW)
	(MW)
	(MW)
	(cfs)

	35
	27.6
	11,259
	31.9
	36.8
	44.3
	18,068
	28.2
	11,444
	32.1
	37.0
	45.1
	18,277

	36
	28.5
	11,271
	32.9
	37.9
	45.8
	18,097
	29.2
	11,455
	33.1
	38.2
	46.6
	18,306

	37
	29.4
	11,279
	33.9
	39.1
	47.3
	18,121
	30.1
	11,464
	34.1
	39.4
	48.1
	18,331

	38
	30.3
	11,284
	34.9
	40.3
	48.8
	18,139
	31.0
	11,470
	35.2
	40.6
	49.7
	18,350

	39
	31.3
	11,287
	36.0
	41.6
	50.3
	18,153
	32.0
	11,473
	36.3
	41.8
	51.2
	18,364

	40
	32.2
	11,288
	37.1
	42.8
	51.8
	18,162
	32.9
	11,474
	37.3
	43.0
	52.7
	18,374

	41
	33.0
	11,259
	38.1
	44.0
	53.3
	18,197
	33.7
	11,445
	38.3
	44.2
	54.3
	18,409

	42
	33.8
	11,230
	39.1
	45.2
	54.9
	18,228
	34.6
	11,415
	39.4
	45.4
	55.8
	18,441

	43
	34.6
	11,201
	40.2
	46.3
	56.4
	18,255
	35.4
	11,386
	40.4
	46.6
	57.4
	18,468

	44
	35.4
	11,172
	41.2
	47.5
	57.9
	18,278
	36.2
	11,357
	41.4
	47.8
	58.9
	18,493

	45
	36.2
	11,144
	42.2
	48.7
	59.4
	18,299
	37.0
	11,328
	42.5
	49.0
	60.5
	18,514

	46
	37.0
	11,139
	43.2
	49.8
	61.0
	18,366
	37.9
	11,324
	43.5
	50.2
	62.1
	18,581

	47
	37.8
	11,135
	44.2
	51.0
	61.9
	18,200
	38.7
	11,319
	44.5
	51.3
	63.0
	18,415

	48
	38.7
	11,129
	45.2
	52.1
	62.7
	18,040
	39.6
	11,314
	45.5
	52.5
	63.8
	18,255

	49
	39.5
	11,124
	46.2
	53.3
	63.5
	17,887
	40.4
	11,308
	46.5
	53.6
	64.7
	18,101

	50
	40.3
	11,118
	47.2
	54.4
	67.5
	18,598
	41.3
	11,303
	47.5
	54.8
	68.7
	18,817

	51
	41.3
	11,154
	48.1
	55.5
	69.8
	18,850
	42.2
	11,339
	48.4
	55.9
	71.1
	19,072

	52
	42.3
	11,187
	49.1
	56.7
	72.1
	19,091
	43.2
	11,373
	49.4
	57.0
	73.4
	19,316

	53
	43.2
	11,219
	50.1
	57.8
	74.5
	19,323
	44.2
	11,405
	50.4
	58.1
	75.8
	19,551

	54
	44.2
	11,249
	51.0
	58.8
	76.5
	19,536
	45.2
	11,436
	51.3
	59.2
	76.5
	19,431

	55
	45.2
	11,278
	52.1
	60.1
	76.5
	19,115
	46.2
	11,466
	52.4
	60.5
	76.5
	18,975

	56
	46.4
	11,343
	53.2
	61.3
	76.5
	18,718
	47.4
	11,531
	53.5
	61.7
	76.5
	18,581

	57
	47.6
	11,404
	54.2
	62.6
	76.5
	18,336
	48.6
	11,593
	54.6
	63.0
	76.5
	18,202

	58
	48.8
	11,461
	55.4
	63.9
	76.5
	17,967
	49.9
	11,652
	55.7
	64.3
	76.5
	17,836

	59
	50.0
	11,515
	56.5
	65.1
	76.5
	17,611
	51.1
	11,707
	56.8
	65.6
	76.5
	17,483

	60
	51.2
	11,567
	57.6
	66.4
	76.5
	17,267
	52.3
	11,760
	57.9
	66.8
	76.5
	17,142

	61
	51.8
	11,532
	58.5
	67.5
	76.5
	16,978
	53.0
	11,724
	58.9
	67.9
	76.5
	16,857

	62
	52.5
	11,498
	59.5
	68.6
	76.5
	16,699
	53.7
	11,690
	59.8
	69.1
	76.5
	16,582

	63
	53.1
	11,466
	60.4
	69.7
	76.5
	16,428
	54.3
	11,657
	60.8
	70.1
	76.5
	16,315

	64
	53.7
	11,434
	61.3
	70.7
	76.5
	16,166
	55.0
	11,625
	61.7
	71.2
	76.5
	16,056

	65
	54.4
	11,405
	62.3
	71.8
	76.5
	15,912
	55.6
	11,595
	62.6
	72.3
	76.5
	15,806

	66
	55.4
	11,448
	63.2
	72.9
	76.5
	15,671
	56.7
	11,639
	63.6
	73.4
	76.5
	15,570

	67
	56.5
	11,490
	64.2
	74.0
	76.5
	15,437
	57.8
	11,682
	64.6
	74.5
	76.5
	15,341

	68
	57.5
	11,532
	65.1
	75.1
	76.5
	15,210
	58.9
	11,724
	65.5
	75.6
	76.5
	15,119

	69
	58.6
	11,571
	66.1
	76.3
	76.5
	14,990
	59.9
	11,764
	66.5
	76.5
	76.5
	14,903

	70
	59.6
	11,610
	67.0
	77.3
	76.5
	14,775
	61.0
	11,803
	32.1
	37.0
	76.5
	14,693


1. Table based on January 2001 data (HDC).  Updated 2006 and 2014 (added Mid-Range).

Justification for Change:
FPOM requested adding PH2 1% mid-range columns since PH2 may be limited to mid-range operation.  See Memo to FPOM from Bonneville Turbine task group for justification.

Comments from others: 

See FPC memo.
9 May 2013 FPOM: Lorz provided change form and supporting documentation.  Wright asked if steps 1-3 could just be accepted now.  Lorz and Fredricks said this is a package deal.  Lorz said going to BOP at PH1 is a contentious issue with some in the Region and they feel the spill is an acceptable trade-off.  Baus and Wright would like to avoid the TMT SOR process but FPOM isn’t quite willing to accommodate that request by parsing out sections of the change form.  There is some fear of kicking the trigger issue down the road and this needs to be dealt with sooner rather than later.  CRITFC, NOAA, USFWS support the change form.  IDFG was absent.  ODFW supported it at the last meeting, but no rep was at the May FPOM.  BPA and USACE need to take this back to their chain of command.  Aside from the fact that this couldn’t be accepted today, Bettin suggested this is a good time to present this.  Fredricks said this is probably the more documented decision FPOM has made and it will likely be included in the 2014 BiOp.  ACTION: FPOM will take the change form to their respective agencies and bring their position back to June FPOM meeting.

22 May 2013 TMT: IDFG (Kiefer), WDFW (Morrill), ODFW (Kruger, VanDyke) agree w/ change form.

13 June 2013 FPOM: NOAA, USFWS, CRITFC, Colville, IDFG and ODFW: support change form as written.  BPA: defer to Corps policy decision and will follow Corps’ lead.  

Corps: decision pending further policy/legal review of proposed operation.

17 Jan 2014 NOAA Memo: 14BON001 - PH2 Mid-Range Operation.  Obviously, we agree with this one but where is it in terms of process?   Action should occur before the juvenile passage season starts.  
22 Jan 2014 FPOM:  Continues to be pending.  RCC looks forward to continuing to coordinate in-season.  This will likely be implemented in-season as it was in 2013.  CRITFC expressed frustration with stalling of this change form.  NOAA believes a decision should be made prior to the juvenile fish passage season.  This issue will be dealt with once Fredricks returns to the office.  Lorz kindly pointed out that NWD has had two years to address this change form and we are no closer to having it finalized.  

13 Feb 2013 FPOM: Still pending further discussions between FPOM, TSP and others considering PNNL data mining results, etc.  Until then, continue to manage via in-season coordination.
5 May 2014 via email: Corps RCC proposed edits (in track changes).
7 May 2014: Approved as revised by FPOM BON Ops Task Group Super-committee – Fredricks, Conder, Wills, Van Dyke, Bettin, Mackey, Baus, Wright, Klatte, Peterson, Hausmann, Guajardo, Traylor, Carroll, Sears.
Record of Final Action:  
� Juvenile spring Chinook: reported as “CollCount” in SMP Smolt Data (query current year BO2 Combined Chinook Yearling), available online at: � HYPERLINK "http://www.fpc.org/smolt/smpsubmitdataquery_2014v7.html" �http://www.fpc.org/smolt/smpsubmitdataquery_2014v7.html� 





� Adult spring Chinook: reported as “Adult Chinook daily” in Corps Adult Fish Count Running Sum Report for Bonneville, available online at: � HYPERLINK "http://www.nwp.usace.army.mil/Missions/Environment/Fish/Data.aspx" �http://www.nwp.usace.army.mil/Missions/Environment/Fish/Data.aspx�





�


Or start April 1?  Continue thru Oct 31?


Why not have these modified ranges effective for the whole period April 1-Oct 31?


�


Propose defining this step as “juvenile trigger” rather than “if adult trigger is not met”.  Clarifies this step is for juveniles and is easier to communicate.


�


Added footnote to provide online data sources for smolt/adult data.  





Assumes only Chinook yearlingscountede only of Chinook yearlings and adults (no jacks).ft constraint Nov 1-Mar 31.  ������������������������������������� and adults (no jacks) are counted.





14BON001 - Page 1 of 4

