Fish Passage Plan (FPP) Change Request Form
Change Form # & Title: 
15BON003 – DSM Orifice Control
Date Submitted: 

October 9, 2014
Project: 


Bonneville Dam
Requester Name, Agency: 
Ben Hausmann, BON Fisheries
Final Action:



FPP Section:
BON Section 2.4.2.4.b.  DSM2 Channel Operation.  
Justification:
Table BON-7 shows orifice gate open/closed positions as a function of forebay level.  In actuality the DSM orifice operation is based upon channel level readings supplied to the PLC (programmable logic control) computer system. When the channel level falls below 64.25”, the program will call for an orifice to open, wait 150 seconds, and repeat if necessary.  If the water level rises to 64.35”, the program will call for an orifice to close. The add-in water is the only other water supply to the DSM, and simply maintains a flow of 60 cfs.  Since the add-in water and the orifice water originate from the PH2 gatewells, the forebay level will indirectly impact these water supplies via head pressure. However, the table as written does not accurately portray this indirect relationship and is misleading as to how the DSM functions.
Proposed Change:
Delete Table BON-7.
2.4.2.4.b. Operation.  Maintain the channel elevation between 64.2–64.4’ as measured at the staff gauge in front of the ERG. 

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	


Comments: 
Record of Final Action:  
15BON003 - Page 1 of 1

