OFFICIAL COORDINATION REQUEST FOR 

NON-ROUTINE OPERATIONS AND MAINTENANCE

COORDINATION TITLE – 15 IHR 003 Unit 5 head gate cylinder replacement
COORDINATION DATE- Feb. 5, 2015 

PROJECT - Ice Harbor Dam
RESPONSE DATE- February 12, 2015 (FPOM Meeting).
Description of the problem – Turbine unit 5 head gate cylinder replacement is tentatively scheduled for June 22-25, 2015. The head gate cylinder installed in gate 5B needs to be replaced because in the past, gatewell slot 5B has had oil sheens and no other cause has been found. While there has not been an oil sheen lately we need to ensure there aren’t any issues with the cylinder. This work cannot be performed in conjunction with annual maintenance because the head gates are required to be down as a hazardous energy control point during annual maintenance. Since Ice Harbor Dam has multiple transformer banks, transmission lines, and redundant switching capability, the remaining turbine units will be available for operation during these tests.  
Type of outage required – Unit 5 outage.
Impact on facility operation – In the event of high river flows, the project may be at generating capacity, and additional spill beyond Fish Passage Plan (FPP) levels would then need to occur in accordance with the FPP Ice Harbor spill pattern tables.
Dates of impacts/repairs – June 22-25, 2015.
Length of time for repairs – June 22-25, 2015.
Expected impacts on fish passage – Since unit 5 is last in operating priority for fish passage, there is minimal impact expected.  The remaining turbine units will operate within the 1% range and in accordance with FPP priority order.
Comments from agencies

Final results
Please email or call with questions or concerns.
Thank you, 

Kenneth R. Fone 
Fisheries Biologist

Ice Harbor Lock and Dam

Ph: (509) 509-543-3208
Email: kenneth.r.fone@usace.army.mil
