OFFICIAL COORDINATION REQUEST FOR 

NON-ROUTINE OPERATIONS AND MAINTENANCE

COORDINATION TITLE- 15TDA08 transformer delivery/installation
COORDINATION DATE-  25 June 2015
PROJECT-  The Dalles Dam
RESPONSE DATE- 9 July 2015 (FPOM)
Description of the problem - The Dalles facility has undergone several major projects which including the replacement of a number of the 2 banks main GSU transformers (T-2 and T-4). Due to their age, condition, and likelihood of failure associated with their age, the older single phase GSU and fish unit transformers should be replaced. Priority of replacement shall be given to those most likely to fail soonest, to those with the most noted issues or concerns as shown by maintenance or operational documentation, or to those where a failure would lead to the largest loss of power generation and transmission. The purpose of this project is to replace the single phase 1954-1958 water cooled Ferranti GSU transformers and 1956 Central Transformer Corp. fish unit transformers with new air cooled GSU transformers over a period of several years. Specifically called out for replacement are: TA, T1, T3, T5, T6, T7, T8.
Type of outage required – Outage required during installation of each transformer. Each transformer serves two main units.  Fish Units may run on TA or T1.
	Transformer
	Generating Units
	Anticipated Schedule

	TA
	Fish Units 
	Jul 2019 (removal)

	Tl
	1, 2
	Jul - Oct 2017

	T3
	5, 6
	Mar - Jun 2018

	T5
	9, 10
	Nov 2018 - Feb 2019

	T6
	11, 12
	Jul - Oct 2018

	T7
	13, 14
	Nov 2017 -Feb 2018

	T8
	15, 16
	Mar -Jun 2019


Impact on facility operation – Each outage is estimated to be 4 months long, during which time those units will not be operating, except for the fish units, which can use either TA or T1.
Units 1 and 2 will be out of service from July – October 2017.  Units 3 and 4 will be operated instead.
Dates of impacts/repairs – July 2017 through August 2019
Length of time for repairs – Each transformer will take about four months.  (see 15TDA08 attachment 1 transformer schedule)
Expected impacts on fish passage – 
Upstream migrants - None, as indicated above, the fish units can use either TA or T1.
Downstream migrants – ITS chain gates will be adjusted as needed as unit priority is adjusted to accommodate unit outages.  Open gates will be moved from Units 1 and 2 to 3 and 4 during the T1 outage.  
Comments from agencies

NOAA  and TDA (Fredricks and Cordie)
-----Original Message-----


From: Gary Fredricks - NOAA Federal [mailto:gary.fredricks@noaa.gov]


Sent: Thursday, June 25, 2015 7:52 AM


To: Mackey, Tammy M NWP


Cc: Lorz, Tom; Trevor Conder - NOAA Federal; Cordie, Robert P NWP


Subject: [EXTERNAL] Re: FPOM: Official Coordination - 15TDA08 transformer installation (UNCLASSIFIED)


Tammy, Overall this shouldn't be a fish passage issue although there probably is some risk associated with no backup transformer for the fish units during the highest adult passage months of the year.  This concern is compounded somewhat by the fact that all of these transformers are in need of replacement.  We should have the emergency AWS system in place by 2017 but as you know, this system is not a full flow replacement for the fish units.   Depending on the opinions of the condition of TA and T1, perhaps T7 should be switched in place of T1 to assure redundancy through October.


Also, I noted that the fish unit transformer TA would be removed.  Does this mean that there would be no redundancy here if T1 died in the future?   Maybe some further discussion is appropriate.  Thanks, Gary

On Mon, Jun 29, 2015 at 9:22 AM, Cordie, Robert P NWP <Robert.P.Cordie@usace.army.mil> wrote:


Classification: UNCLASSIFIED


Caveats: NONE


There will still be redundancy with a bus tie to another transformer bank. It will be through a different line for improved redundancy in case line 1 fails.


More explanation at FPOM.

-----Original Message-----

From: Gary Fredricks - NOAA Federal [mailto:gary.fredricks@noaa.gov] 

Sent: Tuesday, June 30, 2015 1:07 PM

To: Cordie, Robert P NWP

Subject: Re: [EXTERNAL] Re: FPOM: Official Coordination - 15TDA08 transformer installation (UNCLASSIFIED)

Bob,  Is this bus tie a future benefit (after all the transformer work) or something you can do now?  In other words, does it affect my concern for the lack of a backup while the work is being done on TA ?  Thanks, Gary

-----Original Message-----
From: Cordie, Robert P NWP 
Sent: Tuesday, June 30, 2015 1:27 PM
To: Gary Fredricks - NOAA Federal
Cc: Mackey, Tammy M NWP
Subject: RE: [EXTERNAL] Re: FPOM: Official Coordination - 15TDA08 transformer installation (UNCLASSIFIED)

Classification: UNCLASSIFIED

Caveats: NONE

Gary, 

Yes it will be a future benefit and no it's not something we can do before the AWS work starts, because it’s a pretty big project.

There are actually 2 projects planned. 1) Fish unit breaker upgrade/replacement (at 10% Plans). 2) powerhouse transformer replacement. 

While discussing the best alternatives for the fish unit breaker upgrades, eliminating TA transformers was brought up.

The latest schedule for transformer installs is summer of 2017. Should put us just after the install of AWS backup. This is preliminary and we'll still need to work through unit outages needed for the transformer install.

Future benefit; we do have a bus tie now from TA (fish units) to T1 (main units 1 and 2). Both TA and T1 use line 1, so there is no redundancy for a line failure. New plans will tie to another line, preferable 230KV on the east end for more flexibility.

Lots more to come...

Final results

Please email or call with questions or concerns.
Thank you, 

Ricardo Walker

PM-E Fisheries
Ricardo.Walker@usace.army.mil

Tammy Mackey

NWP Operations Division Fishery Section

Columbia River Coordination Biologist

503-961-5733 
Tammy.m.mackey@usace.army.mil 

