# FPP Change Request Form

Change Form # & Title:	15IHR006 – Unit 3 Fixed Blade 1% Range Table

Date Submitted:		April 20, 2015

Project:			IHR

Requester Name, Agency:	Greg Moody, NWW- OD

Final Action:

FPP Section:  Reference tables for turbine unit 1% ranges at the rear of the Ice Harbor Dam section in the FPP.

Justification for Change:  Adding an additional turbine unit 1% range Table IHR-7 to document lower and upper 1% efficiency range for Unit 3 with and without STSs, moving from a Kaplan to a fixed blade operation.

This testing was done in March 2015 by HDC, after the runner blades were welded.

Proposed Changes:

See new Table IHR-7 below.

*Changes the spill pattern table numbers by 1.

Comments from others:

Record of Final Action:

Table IHR-7.  Ice Harbor Dam Turbine Unit 3 Power (MW) and Flow (cfs) at Upper and Lower Limits of the ±1% Peak Efficiency Range. a

|  | Turbine Unit 3 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Project Head (feet) | with STSs |  |  |  | No STSs |  |  |  |
|  | 1% Lower Limit |  | 1% Upper Limit |  | 1% Lower Limit |  | 1% Upper Limit |  |
|  | (MW) | (cfs) | (MW) | (cfs) | (MW) | (cfs) | (MW) | (cfs) |
| 85 | 70.9 | 11,452 | 75.2 | 12,141 | 69.8 | 11,404 | 74.1 | 12,100 |
| 86 | 71.9 | 11,471 | 76.1 | 12,140 | 70.8 | 11,423 | 75.0 | 12,098 |
| 87 | 72.9 | 11,490 | 77.0 | 12,139 | 71.8 | 11,442 | 75.9 | 12,097 |
| 88 | 73.9 | 11,508 | 77.9 | 12,137 | 72.8 | 11,460 | 76.8 | 12,096 |
| 89 | 74.9 | 11,526 | 78.9 | 12,136 | 73.8 | 11,477 | 77.7 | 12,094 |
| 90 | 75.9 | 11,542 | 79.8 | 12,134 | 74.7 | 11,494 | 78.6 | 12,092 |
| 91 | 77.1 | 11,593 | 81.3 | 12,226 | 75.9 | 11,544 | 80.1 | 12,184 |
| 92 | 78.3 | 11,642 | 82.8 | 12,316 | 77.1 | 11,593 | 81.6 | 12,274 |
| 93 | 79.5 | 11,690 | 84.4 | 12,404 | 78.3 | 11,641 | 83.1 | 12,362 |
| 94 | 80.7 | 11,737 | 85.9 | 12,490 | 79.5 | 11,688 | 84.6 | 12,447 |
| 95 | 81.9 | 11,783 | 87.4 | 12,575 | 80.6 | 11,734 | 86.1 | 12,531 |
| 96 | 82.4 | 11,732 | 87.8 | 12,495 | 81.1 | 11,683 | 86.5 | 12,452 |
| 97 | 82.9 | 11,682 | 88.2 | 12,417 | 81.7 | 11,633 | 86.9 | 12,374 |
| 98 | 83.5 | 11,633 | 88.5 | 12,340 | 82.2 | 11,584 | 87.2 | 12,297 |
| 99 | 84.0 | 11,585 | 88.9 | 12,265 | 82.7 | 11,536 | 87.6 | 12,223 |
| 100 | 84.5 | 11,537 | 89.3 | 12,192 | 83.2 | 11,489 | 88.0 | 12,149 |
| 101 | 85.4 | 11,549 | 90.3 | 12,210 | 84.1 | 11,500 | 89.0 | 12,168 |
| 102 | 86.4 | 11,560 | 91.4 | 12,229 | 85.0 | 11,511 | 90.0 | 12,186 |
| 103 | 87.3 | 11,571 | 92.4 | 12,247 | 85.9 | 11,522 | 91.0 | 12,204 |
| 104 | 88.2 | 11,582 | 93.4 | 12,265 | 86.9 | 11,533 | 92.0 | 12,222 |
| 105 | 89.2 | 11,593 | 94.5 | 12,282 | 87.8 | 11,544 | 93.1 | 12,239 |

- Prepared by HDC, March 2015, for Unit 3 with fixed blades.  Based on 1956 Model Test and 2006 Unit 3 STS Index Test w/ STS adjustment factor.