# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:	17IHR007 – Unit 5 Operating Range w/ Welded Blades

Date Submitted:		April 21, 2017

Project:			IHR

Requester Name, Agency:	NWW

Final Action:

FPP Section:  IHR 4.2. Turbine Unit Operating Range.

Justification for Change:  Unit 5 blades were welded in 2016. This new table defines the new, restricted operating range for Unit 5 with welded blades.

Proposed Change:  Add new Table IHR-9.

Table IHR-9.  Ice Harbor Dam Turbine Unit 5 Power (MW) & Flow (kcfs) at Upper and Lower Limits of Restricted Operating Range. a

| Project | Turbine Unit 5 with STS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Head | Lower Limit a |  | Peak Efficiency |  | Upper Limit a |  |
| (ft) | MW | kcfs | MW | kcfs | MW | kcfs |
| 75 | 72.5 | 13.2 | 74.6 | 13.4 | 76.1 | 13.9 |
| 76 | 73.6 | 13.2 | 75.7 | 13.4 | 77.2 | 13.9 |
| 77 | 74.7 | 13.2 | 76.8 | 13.4 | 78.4 | 13.9 |
| 78 | 75.8 | 13.2 | 77.9 | 13.4 | 79.5 | 13.9 |
| 79 | 76.9 | 13.2 | 79 | 13.5 | 80.6 | 13.9 |
| 80 | 77.9 | 13.3 | 80 | 13.5 | 81.7 | 13.9 |
| 81 | 78.8 | 13.2 | 81.1 | 13.5 | 82.9 | 13.9 |
| 82 | 79.7 | 13.2 | 82.2 | 13.5 | 83.8 | 13.9 |
| 83 | 80.6 | 13.2 | 83.3 | 13.5 | 84.7 | 13.8 |
| 84 | 81.5 | 13.2 | 84.4 | 13.5 | 85.6 | 13.8 |
| 85 | 82.4 | 13.1 | 85.5 | 13.5 | 87.5 | 13.9 |
| 86 | 83.8 | 13.2 | 86.6 | 13.5 | 88.5 | 13.9 |
| 87 | 85.2 | 13.2 | 87.8 | 13.5 | 89.5 | 13.9 |
| 88 | 86.6 | 13.3 | 88.9 | 13.5 | 90.5 | 13.9 |
| 89 | 88 | 13.3 | 90.1 | 13.5 | 91.5 | 13.9 |
| 90 | 89.4 | 13.4 | 91.2 | 13.5 | 92.5 | 13.9 |
| 91 | 90.4 | 13.4 | 92.4 | 13.5 | 93.7 | 13.9 |
| 92 | 91.5 | 13.4 | 93.5 | 13.5 | 94.9 | 13.9 |
| 93 | 92.5 | 13.4 | 94.6 | 13.5 | 96 | 13.9 |
| 94 | 93.6 | 13.4 | 95.8 | 13.6 | 97.2 | 13.9 |
| 95 | 94.6 | 13.4 | 96.9 | 13.6 | 98.4 | 13.9 |
| 96 | 95.5 | 13.4 | 98 | 13.6 | 99.6 | 13.9 |
| 97 | 96.3 | 13.3 | 99.1 | 13.6 | 100.8 | 14.0 |
| 98 | 97.1 | 13.3 | 100.3 | 13.6 | 102.1 | 14.0 |
| 99 | 97.9 | 13.3 | 101.4 | 13.6 | 103.3 | 14.0 |
| 100 | 98.7 | 13.2 | 102.5 | 13.6 | 104.5 | 14.0 |
| 101 | 99.8 | 13.2 | 103.6 | 13.6 | 105.7 | 14.0 |
| 102 | 100.9 | 13.3 | 104.6 | 13.6 | 106.9 | 14.0 |
| 103 | 102 | 13.3 | 105.7 | 13.6 | 108. 1 | 14.1 |
| 104 | 103.2 | 13.3 | 106.8 | 13.6 | 109.4 | 14.1 |
| 105 | 104.3 | 13.3 | 107.8 | 13.6 | 110.6 | 14.1 |

a. Unit 5 has welded runner blades (2016) and is restricted to a smaller operating range. Table values based on the

1962 Model Test, 2006 Unit 6 Index Test, and 2017 Unit 8 Abbrev. Index Test.

Comments:

Record of Final Action: