# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title:	17LWG008 – Units 1 & 2 Priority

Date Submitted:		April 21, 2017

Project:			LWG

Requester Name, Agency:	Rich Hilt, COE LWG and Ann Setter, COE NWW

Final Action:

FPP Section:  Table LWG-5. Unit Priority Order.  Table LWG-6. Units 1, 2, 3 1% Range.

Justification for Change:  Refer to MOC 17 LWG 01 and MFR 17 LWG 03 for the specific details of unit 2 maintenance.  Unit 2 returned to service as a fixed-blade unit on April 13, 2017.  Unit 1 is currently OOS for turbine repair; when it returns to service, it will have full Kaplan capabilities (estimated RTS of 14 July 2017).

Unit 2 will require an index test to verify operating conditions.  Until index testing is completed, Unit 2 will be run like Unit 1 was when it operated as a fixed blade unit with an operating range of 125-129 MW (17.8 to 18.4 KCFS of flow based on 100 ft of head in Table LWG-6).

With the return to service of Unit 2 with fixed blades and Unit 1 as a fully adjustable Kaplan, the Unit priority order needs to be modified. This change form modifies Table LWG-5 and footnotes for Table LWG-6 to reflect these changes.

Proposed Change:   See below for edits to existing text in track changes.

Table LWG-5.  Lower Granite Dam Turbine Unit Priority Order.

| Season | Duration | Unit Priority |
| --- | --- | --- |
| March 1 – December 15 Fish Passage Season | Start Units | 1, 3, then 4-6 any order, then 2 a |
|  | Stop Units b | 4-6 any order, then 3, 2 b, 1 |
| December 16 – end of February Winter Maintenance Period | Stop/Start Units | Any Order |

a. Unit 2 has fixed Kaplan blades (non-adjustable) and is restricted to operate in the upper 1% range.  The priority order minimizes Unit 2 starts/stops and allows for the longest runtime once Unit 2 started.

b. Stop units in reverse Start order, except run Unit 2 as long as BPA load request and required spill can be met.  Unit 2 will be turned off prior to unit 1, provided unit 1 is operable.

Footnote to:

Table LWG-6.  Lower Granite Dam Turbine Units 1, 2b, and 3 Power (MW) & Flow (kcfs) at ±1% of Peak Efficiency (1% Range).

b. Unit 2 has fixed runner blades (2017) and is restricted to a smaller operating range in the upper 1% (approximately 17–19 kcfs).

Comments:

From: Bill Hevlin - NOAA Federal

To: Setter, Ann L CIV USARMY CENWW (US)

Cc: Bill Hevlin

Subject: Re: [Non-DoD Source] Re: FPP change forms

Date: Tuesday, April 25, 2017 4:57:25 PM

Yes, Ann, that is the correction that made sense to me. Unit one would usually be the last one off because flow

through it can be varied and still stay in the 1%, and that it provides the strongest downstream current along the

south shore wall.

bill

On Tue, Apr 25, 2017 at 10:52 AM, Setter, Ann L CIV USARMY CENWW (US) <Ann.L.Setter@usace.army.mil

<mailto:Ann.L.Setter@usace.army.mil> > wrote:

Bill:

I agree, looks like someone got an edit mixed up there. Does this look more like what you would find

acceptable?

Table LWG-5.  Lower Granite Dam Turbine Unit Priority Order.

| Season | Duration | Unit Priority |
| --- | --- | --- |
| March 1 – December 15 Fish Passage Season | Start Units | 1, 3, then 4-6 any order, then 2 a |
|  | Stop Units b | 4-6 any order, then 3, 2 b, 1 |
| December 16 – end of February Winter Maintenance Period | Stop/Start Units | Any Order |

a. Unit 2 has fixed Kaplan blades (non-adjustable) and operates in the upper 1% range.  The priority order minimizes Unit 2 starts/stops and allows for the longest runtime once Unit 2 is started.

b. Stop units in reverse Start order, except run Unit 2 as long as BPA load request and required spill can be met.

Ann

-----Original Message-----

From: Bill Hevlin - NOAA Federal [mailto:bill.hevlin@noaa.gov <mailto:bill.hevlin@noaa.gov> ]

Sent: Tuesday, April 25, 2017 10:01 AM

To: Setter, Ann L CIV USARMY CENWW (US) <Ann.L.Setter@usace.army.mil

<mailto:Ann.L.Setter@usace.army.mil> >

Cc: Bill Hevlin <bill.hevlin@noaa.gov <mailto:bill.hevlin@noaa.gov> >

Subject: [Non-DoD Source] Re: FPP change forms

Hi Ann,

In the modified table for Lower Granite turbine operation priority during the fish passage season, in the line for

stop units, turbine 2 is the last off, but I was thinking that unit one should be the last off, due it priority for adult

passage and ability to vary flow due to restored kaplan status. What do you think?

bill

Record of Final Action: