## Slide 1: What happens in a Doble Outage
Greg Brooks, P.E.
Chief of maintenance Engineering
Hydropower Test and Evaluation
(formerly 8 years as test engineer)
Walla Walla District
Date: 8 October 2020

## Slide 2: Conditions
Fully exposed to weather
22’ to top work area
Lots of trip hazards
    Requires fall protection
High Voltage bushing 35’ high
    Requires a man lift
Single phase transformers
    Three combine to make T1 or T2
    Each phase has 4 doghouses where electrical connections are made
35’ High
22’ High
Doghouse
HV Bushing
One Phase of Three

## Slide 3: Outage sequence HIGHLIGHTS
Day 1 – SETUP CLEARANCES & ISOLATE
  Open BPA line breaker
  Open bus at deck level and connect grounds
  Open each doghouse (12 x 22 bolts)
  In each doghouse, unbolt all the flex leads (12 x 48 bolts)
  Tie back or remove the leads depending on the design
Connect Ground Cables
Unbolt and remove connections
Unbolt and remove doghouse covers

## Slide 4: Outage sequence HIGHLIGHTS
Day 2 & 3 – PERFORM TESTS
  14 rearrangements of test leads
  Power Factor Tests
  Winding Resistance Tests
  Turns Ratio Tests
  Corrective Maintenance
Day 4 – RESTORE
  Reconnect
  Seal up covers
  Remove safe clearance
  Reenergize
Tracking
Failure in service from undetected water and tracking

## Slide 5: Why every 3 years?
Lower Snake have less redundancy
    Only two transformers, T1 and T2 (3 single phases combine to make one transformer)
    As seen at Little Goose, one failure can force a plant onto diesel
  Oil filled transformers (10,000 gallons per phase)
    We don’t what them to catastrophically fail
  500KV high side -> higher risk
  History of frequent bushing problems in low side bus
  Advanced age
  Management risk-based decision

## Slide 6: Improvements – what we’ve been up to
Upgraded Doble Test Set (Doble M7100)
    Combines power factor, turns ratio, winding resistance
    Less setup and take down time
    Faster operation
Improved doghouse covers
    Hinged and latched - No more bolts!
    Drip lips for better weather protection
New deck level bus access covers
    No bolts
    Faster inspections
Better weather seals
    Keep water out
Better drains
    Let water out
Walkways at the top
    Little Goose is soon to pilot

## Slide 7: Discussion