# Fish Passage Plan (FPP) Change Form

Change Form # & Title: 	21IHR005 – Unit 4 Operating Range

Date Submitted:		June 7, 2021

Project:			Ice Harbor Dam

Requester Name, Agency:	Lisa Wright, Corps

Final Action:

FPP Section:  Table IHR-5 – Turbine Unit Operating Ranges.

Justification for Change:

This Change Form adds the official 1% operating range values for Unit 4 with hydraulically locked blades based on index testing performed in February 2021.

Proposed Change:

See next page.

Comments:

Record of Final Action:

- Proposed Change:

Add Unit 4 range to Table IHR-5 – see next page in red text:

Table IHR-5. Ice Harbor Dam Turbine Unit Power (MW) and Flow (cfs) at ±1% of Peak Turbine Efficiency (Lower and Upper Limits of 1% Range) and Operating Limits. a

| Project | IHR Unit 1 – with STS |  |  |  |  |  |  | IHR Unit 1 – No STS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head | 1% Lower Limit |  |  | 1% Upper Limit |  | Operating Limit b |  | 1% Lower Limit |  | 1% Upper Limit |  | Operating Limit b |  |
| (feet) | MW |  | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs | MW | cfs |
| 85 | 51.7 |  | 8,417 | 83.6 | 13,590 | 92.8 | 16,053 | 51.9 | 8,340 | 89.9 | 14,452 | 102.6 | 16,859 |
| 86 | 52.6 |  | 8,443 | 84.6 | 13,585 | 94.3 | 16,077 | 52.7 | 8,367 | 91.0 | 14,447 | 103.1 | 16,715 |
| 87 | 53.4 |  | 8,469 | 85.6 | 13,580 | 95.7 | 16,099 | 53.5 | 8,392 | 92.0 | 14,441 | 103.6 | 16,568 |
| 88 | 54.2 |  | 8,494 | 86.6 | 13,574 | 97.3 | 16,144 | 54.3 | 8,417 | 93.1 | 14,436 | 104.1 | 16,420 |
| 89 | 55.0 |  | 8,518 | 87.6 | 13,569 | 99.0 | 16,187 | 55.1 | 8,441 | 94.2 | 14,430 | 104.5 | 16,252 |
| 90 | 55.8 |  | 8,542 | 88.6 | 13,563 | 100.1 | 16,158 | 55.9 | 8,465 | 95.3 | 14,424 | 104.5 | 16,034 |
| 91 | 56.5 |  | 8,548 | 89.8 | 13,585 | 101.0 | 16,058 | 56.6 | 8,471 | 96.5 | 14,448 | 104.5 | 15,822 |
| 92 | 57.1 |  | 8,554 | 90.9 | 13,607 | 101.9 | 15,960 | 57.3 | 8,477 | 97.8 | 14,471 | 104.5 | 15,614 |
| 93 | 57.8 |  | 8,559 | 92.1 | 13,628 | 102.8 | 15,864 | 58.0 | 8,482 | 99.0 | 14,494 | 104.5 | 15,411 |
| 94 | 58.5 |  | 8,565 | 93.2 | 13,649 | 103.6 | 15,769 | 58.6 | 8,488 | 100.3 | 14,516 | 104.5 | 15,213 |
| 95 | 59.2 |  | 8,570 | 94.4 | 13,669 | 104.5 | 15,675 | 59.3 | 8,493 | 101.5 | 14,537 | 104.5 | 15,019 |
| 96 | 59.9 |  | 8,589 | 95.3 | 13,662 | 104.5 | 15,425 | 60.1 | 8,511 | 102.5 | 14,530 | 104.5 | 14,845 |
| 97 | 60.7 |  | 8,607 | 96.3 | 13,655 | 104.5 | 15,180 | 60.8 | 8,529 | 103.6 | 14,522 | 104.5 | 14,676 |
| 98 | 61.5 |  | 8,624 | 97.3 | 13,648 | 104.5 | 14,941 | 61.6 | 8,546 | 104.6 | 14,515 | 104.5 | 14,509 |
| 99 | 62.2 |  | 8,641 | 98.2 | 13,641 | 104.5 | 14,708 | 62.4 | 8,563 | 105.7 | 14,508 | 104.5 | 14,347 |
| 100 | 63.0 |  | 8,658 | 99.2 | 13,634 | 104.5 | 14,481 | 63.1 | 8,580 | 106.7 | 14,500 | 104.5 | 14,187 |
| 101 | 64.0 |  | 8,707 | 99.9 | 13,590 | 104.5 | 14,318 | 64.1 | 8,629 | 107.4 | 14,454 | 104.5 | 14,037 |
| 102 | 65.0 |  | 8,756 | 100.6 | 13,547 | 104.5 | 14,158 | 65.2 | 8,677 | 108.2 | 14,408 | 104.5 | 13,890 |
| 103 | 66.0 |  | 8,804 | 101.3 | 13,505 | 104.5 | 14,001 | 66.2 | 8,725 | 108.9 | 14,363 | 104.5 | 13,746 |
| 104 | 67.0 |  | 8,850 | 102.0 | 13,463 | 104.5 | 13,847 | 67.2 | 8,771 | 109.7 | 14,319 | 104.5 | 13,605 |
| 105 | 68.0 |  | 8,896 | 102.6 | 13,422 | 104.5 | 13,697 | 68.2 | 8,816 | 110.4 | 14,275 | 104.5 | 13,466 |
|  | IHR Unit 2 c – with STS |  |  |  |  |  |  | IHR Unit 2 c – No STS |  |  |  |  |  |
| 85 | 77.0 |  | 12,134 | 86.8 | 13,678 | 89.4 | 14,254 | 78.2 | 12,244 | 89.2 | 13,967 | 91.2 | 14,392 |
| 86 | 77.9 |  | 12,112 | 88.1 | 13,698 | 90.8 | 14,290 | 79.2 | 12,241 | 90.5 | 13,987 | 92.7 | 14,389 |
| 87 | 79.3 |  | 12,166 | 89.1 | 13,670 | 92.2 | 14,333 | 80.9 | 12,344 | 91.9 | 14,022 | 94.2 | 14,509 |
| 88 | 80.2 |  | 12,143 | 90.4 | 13,687 | 93.6 | 14,363 | 81.9 | 12,338 | 93.2 | 14,041 | 95.6 | 14,511 |
| 89 | 81.6 |  | 12,194 | 91.1 | 13,614 | 95.0 | 14,474 | 83.2 | 12,377 | 94.5 | 14,058 | 97.1 | 14,500 |
| 90 | 82.5 |  | 12,170 | 92.4 | 13,631 | 96.4 | 14,508 | 84.2 | 12,371 | 95.9 | 14,090 | 98.6 | 14,619 |
| 91 | 83.9 |  | 12,230 | 93.7 | 13,659 | 97.8 | 14,526 | 85.5 | 12,408 | 96.9 | 14,062 | 100.1 | 14,643 |
| 92 | 84.8 |  | 12,216 | 95.0 | 13,686 | 99.2 | 14,536 | 86.9 | 12,458 | 97.5 | 13,977 | 101.5 | 14,762 |
| 93 | 85.8 |  | 12,217 | 96.7 | 13,769 | 100.6 | 14,623 | 87.9 | 12,449 | 99.5 | 14,092 | 103.0 | 14,787 |
| 94 | 86.8 |  | 12,217 | 97.8 | 13,765 | 102.0 | 14,619 | 88.9 | 12,441 | 100.5 | 14,064 | 103.5 | 14,628 |
| 95 | 88.1 |  | 12,258 | 99.3 | 13,817 | 103.2 | 14,568 | 90.2 | 12,474 | 101.5 | 14,037 | 103.5 | 14,300 |
| 96 | 89.1 |  | 12,255 | 100.3 | 13,796 | 103.5 | 14,469 | 91.2 | 12,474 | 102.8 | 14,061 | 103.5 | 14,024 |
| 97 | 90.1 |  | 12,251 | 101.6 | 13,815 | 103.5 | 14,229 | 92.5 | 12,515 | 103.8 | 14,044 | 103.5 | 13,782 |
| 98 | 91.1 |  | 12,248 | 103.3 | 13,888 | 103.5 | 13,977 | 93.2 | 12,475 | 105.5 | 14,121 | 103.5 | 13,576 |
| 99 | 92.7 |  | 12,323 | 104.2 | 13,852 | 103.5 | 13,744 | 94.2 | 12,475 | 106.8 | 14,143 | 103.5 | 13,404 |
| 100 | 94.1 |  | 12,371 | 105.2 | 13,830 | 103.5 | 13,543 | 94.9 | 12,435 | 108.5 | 14,217 | 103.5 | 13,254 |
| 101 | 94.7 |  | 12,316 | 106.9 | 13,902 | 103.5 | 13,365 | 95.5 | 12,380 | 109.8 | 14,234 | 103.5 | 13,114 |
| 102 | 95.7 |  | 12,313 | 107.9 | 13,883 | 103.5 | 13,205 | 97.2 | 12,467 | 111.2 | 14,263 | 103.5 | 12,979 |
| 103 | 97.0 |  | 12,348 | 109.5 | 13,940 | 103.5 | 13,061 | 98.2 | 12,464 | 113.2 | 14,368 | 103.5 | 12,852 |
|  | IHR Unit 3 c |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Out of service until 2021 for installation of a new adjustable-blade runner design. |  |  |  |  |  |  |  |  |  |  |  |

| Project |  | IHR Unit 4 (Locked Blades) – with STS |  |  |  |  |  |  |  |  |  |  |  | IHR Unit 4 (Locked Blades) – no STS |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head |  | Lower Limit |  |  |  | Peak Efficiency |  |  |  | Upper Limit |  |  |  | Lower Limit |  |  |  | Peak Efficiency |  |  | Upper Limit |  |  |  |
| (feet) |  | MW |  | cfs |  | MW |  | cfs |  | MW |  | cfs |  | MW |  | cfs |  | MW | cfs |  | MW |  | cfs |  |
| 85 |  | 76.6 |  | 12,206 |  | 79.6 |  | 12,608 |  | 83.5 |  | 13,302 |  | 77.7 |  | 12,161 |  | 81.3 | 12,650 |  | 84.7 |  | 13,251 |  |
| 86 |  | 78.0 |  | 12,265 |  | 80.8 |  | 12,632 |  | 84.4 |  | 13,277 |  | 79.1 |  | 12,221 |  | 82.5 | 12,668 |  | 85.6 |  | 13,227 |  |
| 87 |  | 79.3 |  | 12,323 |  | 81.9 |  | 12,656 |  | 85.3 |  | 13,252 |  | 80.5 |  | 12,279 |  | 83.6 | 12,685 |  | 86.6 |  | 13,203 |  |
| 88 |  | 80.7 |  | 12,379 |  | 83.1 |  | 12,678 |  | 86.2 |  | 13,228 |  | 81.9 |  | 12,335 |  | 84.8 | 12,702 |  | 87.5 |  | 13,178 |  |
| 89 |  | 82.1 |  | 12,433 |  | 84.3 |  | 12,700 |  | 87.1 |  | 13,204 |  | 83.3 |  | 12,389 |  | 86.0 | 12,718 |  | 88.4 |  | 13,155 |  |
| 90 |  | 83.4 |  | 12,486 |  | 85.5 |  | 12,721 |  | 88.1 |  | 13,180 |  | 84.7 |  | 12,442 |  | 87.1 | 12,733 |  | 89.4 |  | 13,131 |  |
| 91 |  | 84.4 |  | 12,491 |  | 86.5 |  | 12,729 |  | 89.2 |  | 13,194 |  | 85.7 |  | 12,447 |  | 88.2 | 12,742 |  | 90.5 |  | 13,145 |  |
| 92 |  | 85.5 |  | 12,496 |  | 87.6 |  | 12,738 |  | 90.3 |  | 13,208 |  | 86.7 |  | 12,452 |  | 89.3 | 12,751 |  | 91.6 |  | 13,159 |  |
| 93 |  | 86.5 |  | 12,500 |  | 88.7 |  | 12,746 |  | 91.5 |  | 13,221 |  | 87.8 |  | 12,456 |  | 90.4 | 12,760 |  | 92.8 |  | 13,172 |  |
| 94 |  | 87.5 |  | 12,504 |  | 89.7 |  | 12,753 |  | 92.6 |  | 13,234 |  | 88.8 |  | 12,460 |  | 91.5 | 12,768 |  | 93.9 |  | 13,185 |  |
| 95 |  | 88.5 |  | 12,508 |  | 90.8 |  | 12,760 |  | 93.7 |  | 13,246 |  | 89.8 |  | 12,464 |  | 92.6 | 12,776 |  | 95.1 |  | 13,197 |  |
| 96 |  | 89.5 |  | 12,511 |  | 91.8 |  | 12,767 |  | 94.9 |  | 13,262 |  | 90.8 |  | 12,468 |  | 93.6 | 12,783 |  | 96.3 |  | 13,214 |  |
| 97 |  | 90.5 |  | 12,514 |  | 92.9 |  | 12,773 |  | 96.0 |  | 13,277 |  | 91.9 |  | 12,471 |  | 94.7 | 12,790 |  | 97.5 |  | 13,229 |  |
| 98 |  | 91.5 |  | 12,517 |  | 94.0 |  | 12,779 |  | 97.2 |  | 13,293 |  | 92.9 |  | 12,473 |  | 95.8 | 12,797 |  | 98.6 |  | 13,245 |  |
| 99 |  | 92.5 |  | 12,519 |  | 95.0 |  | 12,785 |  | 98.4 |  | 13,307 |  | 93.9 |  | 12,476 |  | 96.9 | 12,803 |  | 99.8 |  | 13,259 |  |
| 100 |  | 93.6 |  | 12,521 |  | 96.1 |  | 12,790 |  | 99.5 |  | 13,321 |  | 95.0 |  | 12,478 |  | 98.0 | 12,809 |  | 101.0 |  | 13,273 |  |
| 101 |  | 94.6 |  | 12,530 |  | 97.1 |  | 12,794 |  | 100.8 |  | 13,348 |  | 96.0 |  | 12,487 |  | 99.0 | 12,812 |  | 102.2 |  | 13,300 |  |
| 102 |  | 95.6 |  | 12,538 |  | 98.1 |  | 12,797 |  | 102.0 |  | 13,374 |  | 97.0 |  | 12,496 |  | 100.0 | 12,814 |  | 103.5 |  | 13,326 |  |
| 103 |  | 96.6 |  | 12,547 |  | 99.1 |  | 12,800 |  | 103.2 |  | 13,399 |  | 98.1 |  | 12,504 |  | 101.1 | 12,817 |  | 104.7 |  | 13,352 |  |
| 104 |  | 97.7 |  | 12,555 |  | 100.1 |  | 12,803 |  | 104.4 |  | 13,424 |  | 99.1 |  | 12,512 |  | 102.1 | 12,819 |  | 106.0 |  | 13,376 |  |
| 105 |  | 98.7 |  | 12,562 |  | 101.2 |  | 12,806 |  | 105.6 |  | 13,449 |  | 100.1 |  | 12,520 |  | 103.1 | 12,821 |  | 107.2 |  | 13,401 |  |
| Project | IHR Units 5, 6 (Locked Blades) – with STS |  |  |  |  |  |  |  |  |  |  |  | IHR Units 5, 6 (Locked Blades) – No STS |  |  |  |  |  |  |  |  |  |  |  |
| Head | Lower Limit |  |  |  | Peak Efficiency |  |  |  | Upper Limit |  |  |  | Lower Limit |  |  |  | Peak Efficiency |  |  |  |  | Upper Limit |  |  |
| (feet) | MW |  | cfs |  | MW |  | cfs |  | MW |  | cfs |  | MW |  | cfs |  | MW |  |  | cfs |  | MW |  | cfs |
| 85 | 82.4 |  | 13,129 |  | 85.5 |  | 13,458 |  | 87.5 |  | 13,933 |  | 79.8 |  | 12,475 |  | 83.3 |  |  | 12,884 |  | 91.0 |  | 14,224 |
| 86 | 83.8 |  | 13,184 |  | 86.6 |  | 13,470 |  | 88.5 |  | 13,916 |  | 81.1 |  | 12,527 |  | 84.6 |  |  | 12,914 |  | 92.0 |  | 14,208 |
| 87 | 85.2 |  | 13,237 |  | 87.8 |  | 13,482 |  | 89.5 |  | 13,900 |  | 82.5 |  | 12,578 |  | 85.8 |  |  | 12,943 |  | 93.1 |  | 14,191 |
| 88 | 86.6 |  | 13,288 |  | 88.9 |  | 13,492 |  | 90.5 |  | 13,884 |  | 83.8 |  | 12,627 |  | 87.1 |  |  | 12,971 |  | 94.1 |  | 14,175 |
| 89 | 88.0 |  | 13,339 |  | 90.1 |  | 13,503 |  | 91.5 |  | 13,867 |  | 85.2 |  | 12,675 |  | 88.3 |  |  | 12,998 |  | 95.1 |  | 14,159 |
| 90 | 89.4 |  | 13,387 |  | 91.2 |  | 13,513 |  | 92.5 |  | 13,851 |  | 86.5 |  | 12,721 |  | 89.6 |  |  | 13,024 |  | 96.2 |  | 14,143 |
| 91 | 90.4 |  | 13,390 |  | 92.4 |  | 13,524 |  | 93.7 |  | 13,867 |  | 87.5 |  | 12,724 |  | 90.6 |  |  | 13,032 |  | 97.4 |  | 14,159 |
| 92 | 91.5 |  | 13,392 |  | 93.5 |  | 13,534 |  | 94.9 |  | 13,883 |  | 88.6 |  | 12,726 |  | 91.7 |  |  | 13,040 |  | 98.6 |  | 14,174 |
| 93 | 92.5 |  | 13,394 |  | 94.6 |  | 13,545 |  | 96.0 |  | 13,897 |  | 89.6 |  | 12,728 |  | 92.8 |  |  | 13,047 |  | 99.9 |  | 14,190 |
| 94 | 93.6 |  | 13,396 |  | 95.8 |  | 13,555 |  | 97.2 |  | 13,912 |  | 90.6 |  | 12,730 |  | 93.9 |  |  | 13,054 |  | 101.1 |  | 14,204 |
| 95 | 94.6 |  | 13,397 |  | 96.9 |  | 13,564 |  | 98.4 |  | 13,926 |  | 91.6 |  | 12,732 |  | 95.0 |  |  | 13,061 |  | 102.3 |  | 14,219 |
| 96 | 95.5 |  | 13,362 |  | 98.0 |  | 13,569 |  | 99.6 |  | 13,943 |  | 92.4 |  | 12,698 |  | 96.0 |  |  | 13,054 |  | 103.6 |  | 14,237 |
| 97 | 96.3 |  | 13,327 |  | 99.1 |  | 13,574 |  | 100.8 |  | 13,960 |  | 93.2 |  | 12,665 |  | 97.0 |  |  | 13,047 |  | 104.8 |  | 14,254 |
| 98 | 97.1 |  | 13,292 |  | 100.3 |  | 13,578 |  | 102.1 |  | 13,976 |  | 93.9 |  | 12,632 |  | 98.0 |  |  | 13,039 |  | 106.1 |  | 14,271 |
| 99 | 97.9 |  | 13,258 |  | 101.4 |  | 13,582 |  | 103.3 |  | 13,991 |  | 94.7 |  | 12,600 |  | 99.0 |  |  | 13,032 |  | 107.4 |  | 14,287 |
| 100 | 98.7 |  | 13,225 |  | 102.5 |  | 13,586 |  | 104.5 |  | 14,007 |  | 95.5 |  | 12,568 |  | 100.0 |  |  | 13,025 |  | 108.7 |  | 14,302 |
| 101 | 99.8 |  | 13,240 |  | 103.6 |  | 13,588 |  | 105.7 |  | 14,026 |  | 96.6 |  | 12,583 |  | 101.1 |  |  | 13,023 |  | 109.9 |  | 14,322 |
| 102 | 100.9 |  | 13,255 |  | 104.6 |  | 13,590 |  | 106.9 |  | 14,044 |  | 97.7 |  | 12,597 |  | 102.1 |  |  | 13,021 |  | 111.2 |  | 14,341 |
| 103 | 102.0 |  | 13,269 |  | 105.7 |  | 13,592 |  | 108.1 |  | 14,063 |  | 98.8 |  | 12,611 |  | 103.1 |  |  | 13,019 |  | 112.5 |  | 14,360 |
| 104 | 103.2 |  | 13,283 |  | 106.8 |  | 13,594 |  | 109.4 |  | 14,081 |  | 99.8 |  | 12,624 |  | 104.1 |  |  | 13,018 |  | 113.7 |  | 14,378 |
| 105 | 104.3 |  | 13,297 |  | 107.8 |  | 13,596 |  | 110.6 |  | 14,098 |  | 100.9 |  | 12,637 |  | 105.1 |  |  | 13,016 |  | 115.0 |  | 14,396 |

- Values provided by HDC (Mar 2007), as updated for Unit 2 with new runner design (Apr 2019) and Units 4, 5, 6 with locked blades (Dec 2019 and Jun 2021). Flow (cfs) was calculated based on turbine efficiency, project head, and power output (MW).

- “Operating Limit” is the maximum safe operating point based on cavitation or generator limit (added Feb 2018). IHR Units 1-3 have a generator limit that restricts turbine output at higher heads. Values shaded in gray indicate the Operating Limit is below the 1% Upper Limit.

- Unit 2 was rebuilt with a new fixed-blade runner design to reduce impacts to fish (completed May 2019). Unit 3 is out of service in 2021 for installation of a new adjustable-blade runner design.

- Units 4, 5, and 6 have locked runner blades and a restricted operating range until the blade seals are repaired or replaced. Operating range values are based on abbreviated index tests for Unit 4 (2021), Unit 5 (2017), and Unit 6 (2019).