## NWP Rogue
Project | Work Package Title | Work type | Description of Unsatisfactory Performance | Consequences of the Unsatisfactory Performance | $ Source
Lost Creek | Cole Rivers Hatchery Water Supply Rehab | DDR / P&S / Replace | The existing steel piping supplies water to our incubation and early rearing facility. The interior surface of the unlined steel pipe is covered with numerous rust nodules that may allow pathogens to grow, contaminating the water supply. | Exposure to pathogens, especially during early development, can cause disease outbreaks leading to high mortality and additional costs to treat these diseases. 360,000 Spring Chinook died in December 2018 due to a buildup of algae and failing equipment which allowed silt and debris into the hatchery's water supply which cutoff oxygen (need to very the cause). | O&M
Applegate | Trap & Haul Facility | DDR / P&S / Construction | Fish elevators failed in FY15. Initial repairs have been accomplished (wire ropes replaced in FY15); long term repairs required. Fish sorter also needed at Applegate. Hatch Facility needs major repair/upgrade to ensure mitigation requirements are met & support recovery of ESA-listed species. The facil is 30 years old. Maint items incl repair & repl of heavy machinery & hatchery equip, repl of liberation truck. Applegate fish collection facil does not function properly to handle sensitive species. This facility is prone to flooding during high releases from the dam (floods almost annually; flows >3kcfs). | Steelhead died when fish elevator failed. Fish sorter will result in significantly reduced fish handling and more effeicient operations. | O&M
Applegate | Cole Rivers Hatchery Roof Replacement | Replace | Hatchery roofs leaks but has been patched. | Unsatisfactory/unsafe work conditions while roof leaking. | O&M

## NWP WVP
Project | Work Package Title | Work type | Description of Unsatisfactory Performance | Consequences of the Unsatisfactory Performance | $ Source
Lookout Point/Dexter | Willamette Hatchery intake structure | P&S / Construction | Sink hole, Screens previously failed& were repaired. New screens required. | II - Medium High | O&M
Detroit/Big Cliff | Marion Forks Circular Ponds | Repair / Replace | The current ponds are painted with a synthetic liner that keeps the concrete from leaking and provides a smooth surface which is beneficial for fish health. The original paint and lining are degraded and threaten the circular pond integrity. | If the paint continues to deteriorate, it will eventually render the ponds unusable, severely impacting the hatchery. Some fish production would not be possible and the Corps would fail to meet its mitigation responsibilities for Willamette Valley Project dams. | O&M
Dexter | Hatchery Water Supply Pipe | P&S / Construction | Water supply pipe has periodic surge, leaks in some valves, visible deformation of pipe; uncertainty as to whether water supply can be shut off under flow in emergency. | Potential dam safety issue, does not meet Dam Safety/Mechanical Design ER. Not found to be a risk driver in 2013 PA. | O&M
Lookout Point/Dexter | Willamette Hatchery Water Well | Study / P&S | Spring 2007, well capacity continues to decline causing cavitation / supersaturation resulting in loss of 600,000 rainbow trout fry. ODFW saving extra eggs at other facilities. Overtap of aquifer by others causing shortage of well capacity. | Moderate - risk of fish kill in hatchery. Not meet Corps mitigation responsibility, possible litigation. | O&M
Foster | South Santiam Fish Hatchery Supply Water Intake Valves | P&S / Repair or Replace | Original valves in poor condition; no longer seat and leak lubricant. No way to inspect exposed piping upstream of valves. The removal of equipment and filling in of diffusion pits improves the collection channel Hydraulics and produces a safer environment for ROV/divers. It will also remove equipment that would otherwise require maintenance and serve as a potential source of oil leaks. | Failure could result in loss of water supply to fish hatchery. | O&M
Cougar | Fish Water Supply |  | Numerous pump failures over the years. |  | O&M
Detroit/Big Cliff | Minto Fish Hopper Hoist |  | Double brake system? |  | O&M
Detroit/Big Cliff | Marion Forks water supply pipe/valves | EDR/DDR / P&S / Repair | Pipe/valves 70 years old, degraded and leaking, recent asbestos removal has exacerbated this issue | ESA compliance, impacts to hatchery mitigaiton and current operations
Cougar | McKenzie Hatchery Water Supply | EDR/DDR / P&S / Repair | The canal that provides water to the hatchery has been dewatered, thus, not providing much water to the facility. | ESA compliance, impacts to hatchery mitigaiton, requires use of another hatchery to maintain current operations.

## NWP COL
Project | Work Package Title | Work type | Description of Unsatisfactory Performance | Consequences of the Unsatisfactory Performance | $ Source
Bonneville | Spillway Fish Elevators | DDR / P&S / Repairs | Fish elevators are non-functional, have not been used in at least 50 years, and are an environmental and safety hazard. Fish elevators need to be decommissioned and removed from the project. The existing areas should be cleaned up and be made available for other uses. | Environmental issues due to potential oil spillage. May have wooden bulkheads that could fail. | O&M
Bonneville | Cascades Island Fish Ladder | Major Overhaul |  |  | O&M
Bonneville | Bradford Island Fish Ladder Exit | P&S / Install New | Bradford Island Fishladder Exit requires expensive O&M dredging. A newly designed and built exit channel would remove the need for maintenance dredging in the future | Repeated bi-annual dredging ($250K every 2 years) is required to keep fish ladder exit area deep enough for adult fish passage. | O&M
Bonneville | Fish Ladder, Bradford Island A Branch Auxiliary water supply conduit (AWS) Joint Repair | P&S / Rehab | The conduit is not watertight and the significant leaks have resulted in a sinkhole and a small geyser that is undermining a sidewalk and potentially the ladder itself. Past repairs have not been able to adequately address the failure. | Failure of this conduit results in a complete stoppage of adult fish passage in the A-branch of the Bradford Island fish ladder. This would violate the Fish Passage Plan/BiOp. | O&M
Bonneville | Fish Ladder, Bradford Island A Branch Fish valves (FV1-2, 3-7, 3-9) | P&S / Rehab | These valves provide all of the water for the A-branch, both for fish attraction and to the diffusers. These valves are original equipment from the 1930s, and are in need of refurbishment. FV 1-2 is currently only used under special circumstances due to its condition. | Failure of these valves results in a complete stoppage of adult fish passage in the A-branch of the Bradford Island fish ladder. This would violate the Fish Passage Plan/BiOp. | O&M
Bonneville | Fish Ladder, Cascades Island Diffusers | P&S / Rehab | Some number of diffusers fail every year. Work arounds are implemented but can only partially address the problem. Structural degradation and aging equipment will soon preclude repair possibilities and will instead require complete replacement. | Failure of one diffuser results in out of criteria status with the Fish Passage Plan/BiOP. Failure of more than one cannot be worked around and will limit or preclude fish passage. | O&M
Bonneville | Cascade Island Fishladder Bridge Replacement | P&S / Repair | Scope is to replace or reinforce Cascade Island Fishladder Bridge to regain lead AASHTO Load Limits. The Cascade Island Fishladder Bridge has been derated to 29T and we can no longer move the 65T crane to the area to perform Fish Ladder Maintenance. | Without the 65T crane the Sea Lion Exclusion Devices cannot be removed and bulkheads placed to dewater the ladder. Maintenance cannot be performed on lower diffuser gates, FV 5-3 or FV 5-4. Should Corrective Maintenance be required and access is not possible the ladder would not meet BiOP requirements. The subsiding area of Cascade Island cannot be accessed for repair. | O&M
Bonneville | Powerhouse 1 Collection Channel (cc) bulkheads | Repair/ Replace | Bonn does not have the ability to dewater the PH1 collection channel. The bulkheads between the cc and tailwater only seal when the cc is watered up. Decades of deffered maintenance means that failure of fishway critical equipment is only a matter of time. | Failure of diffusers or gratings could result in entrapment of fish or the inability to properly control entrance differentials to the Bradford Island fishway. | O&M
Bonneville | Powerhouse 1 Collection Channel (cc) control system | Replace | PH1 CC control system is very old (25 years or more) and obsolete - replacement parts are not available. Programming platform is DOS based. Gate level transducers are nearing "end-of-life" and drifting. | Failure of the control system would prevent the fish passage system from meeting requirements set forth by the FPP. | O&M
Bonneville | Fish Ladders, Cascades Island Fishway Report - Phase 2 | Study / Report | Diffuser structural problems and air entrainment by fish valves that causes gas supersaturation of fishway above TDG limits (Fish Valve 1-1, 4-3, 4-4, 5-3, 5-4) | We will be unable to meet the BiOp and Fish Passage Plan requirements for passage of the thirteen ESA listed species and all other migrating fish if failure continues at current rate. | O&M
Bonneville | Fish Viewing Roof Replacement |  | Replace/repair leaking membrane and gutter system on Washington Shore Fish viewing building. | Water intrusion during rainstorms creates slip hazards in the building and creates a poor presentation of USACE to the public.
John Day | Submerged Traveling Screen (STS) Rehab | DDR / P&S / Repair | Submerged Traveling Screen (STS) need major overhaul (corrosion, bearings, etc.). There are 48 working screens plus one extra screen (49 total). | STS failure causes Main Unit shutdown. | O&M
John Day | Bonneville Hatchery Wells (Johh Day mitigation) | P&S / Construction | Well Field Production (Water) has decreased below MOU required level. Continued decrease in production projected. Well Field Production (Water) has decreased below MOU required level. Continued decrease in production projected. | Moderate - Impacts hatchery operations including reducing overall production of fish, limiting or changing fish species production, possible early release of fish from hatchery to river. No system back-up, except pumping river water. Need intertie betwn B1 & B2 wells | O&M
John Day | AWS Rehab Remaining 2 Fish Unit Turbine Pumps (SAP Name: Fish HYD Pumps U1 & U2 Rehabilitiation?) | Rehab | Age of turbines and possibility of failure leads to requirement for rehab. All 3 installed at same time, one has failed and pump 2 is near failure. One remaining functional pump will likely fail soon. | Risk that loss of fish turbines would take adult ladder out of performance criteria. Possible delay to adult passage times; would violate meeting the BiOp/ESA. | O&M
John Day | Stabilize North fish ladder and South channel basalt rock walls. | Rehab | Geotechnical work, requiring structural support of walls at identified vulnerable areas. Small areas of rock fall have already occurred. Identified vulnerable areas could result in ladder blockage from large scale rock fall. | Ladder blockage could result in blocking up to 30% of the salmon run during times of highest use of north ladder. | O&M
John Day | JBS Expansion Joint | Repair / Replace | Needs to be re-designed for the larger/wider cover plates/ recessed wall to stop water leaks |  | O&M
John Day | Bonneville Hatchery Well Field (Johh Day mitigation) | Study/Repair or Replace Wells | Hatchery well field has iron bacteria problem and local well gravel pack silting. | Critical - loss of fish production, failure to meet contractual obligations with ODFW. | O&M
John Day | North Ladder Elevator |  |  | Used by CRITFC to collect lamprey in support of the Tribal Translocation Program and Fish Accords. | O&M
The Dalles | Fishway Diffuser | Removal/Rehab | Removal of east fishway collection channel unused diffuser valves and permanent closure. Possible removal of east entrance, junction pool, east lower ladder and north ladder diffuser valves and maintain permanently opened. | The Dalles east fishway passes approximately 80% all Columbia river migrating fish, including 7 ESA listed species. Operation of the east fishway auxiliary water system has changed since original design, with the latest fish passage radiotelemtry information. Collection channel valves are always closed due to this changed operation. Maintenance is unnecessary if not used. Permanent closure method is required due to the degraded state of many of these valves. Failure of unused diffuser valves can result in blown diffuser grating resulting in catastrophic fish kill of ESA listed species. | O&M
The Dalles | Fishway Arc Flash Mitigation |  | Several pieces of equipment have high arc flash incident energies (Cat 4). Arc Flash Hazard Analysis completed in March 2015 by HDR identified several pieces of equipment with high arc flash incident energies. The analysis provided recommended mitigation to lower the arc flash incident energy to a safe level for personnel. The majority of the recommended mitigation is being completed under a power funded contract; however, there is equipment remaining that requires mitigation which can not be power funded. The equipment with high arc flash incident energies are at substations FSQA, FSQ1, FSQ2, FSQ4 and FSQ6. These substations provide power to the fishway (lighting, gate controls, portable pumps, heating, and receptacles). To mitigate the arc flash energy at these locations a maintenance switch and indicating light would be installed providing an input to the protective relay associated with the feed to the substation. During maintenance or switching operations the maintenance mode would be used to lower the arc flash incident energy from category 4 to category 1. | Operations or maintenance on these substations could result in an arc flash accident. An arc flash accident with incident energy of category 4 would result in a serious injury or fatality to the personnel involved. The substation equipment would require replacement due to excessive damage and possible fire. If Maintence switches are not installed, personnel will continue to be at an elevated rist of injury. | O&M
The Dalles | Fishway Automation |  | Critical components are past useful life and unsupported by OEM. Originally installed fiber optic cable is failing. Replacement parts are no longer available for purchase. Procure and install new fishway automation for all entrance and exit weirs. | This fishway passes approx 80% of total adult fish passage upstream on the Columbia River. If water levels in the fishladder cannot be regulated then fish passage will be negatively impacted. Seven ESA listed salmonid species pass through this system. | O&M

## NWW
Project | Item | Location | Work Item | Comment
McNary | 1 | Oregon Fishway | Repair/replace three south shore AWS pumps. | Condition of pumps results in being off line often for repairs. Pumps 1 & 3 currently OOS requiring closing of some entrances to maintain passage criteia
McNary | 2 | Oregon Fishway | Rejuvenate dewatering system; replace rotovalves, slide gates | Project cannot currently dewater south shore fishway to affect repairs. See MNA WA&OR_FishLadder_Condition Assessment.pdf
McNary | 3 | Oregon Fishway | Rejuvenate dewatering system; Replace transverse stoplog guides. | See MNA WA&OR_FishLadder_Condition Assessment.pdf
McNary | 4 | Oregon Fishway | Rejuvenate dewatering system; Rehabilitate all transverse stoplogs. | See MNA WA&OR_FishLadder_Condition Assessment.pdf
McNary | 5 | Oregon Fishway | Rejuvenate dewatering system; Rehabilitate all floating weirs and guides | See MNA WA&OR_FishLadder_Condition Assessment.pdf
McNary | 6 | Oregon Fishway | Permanently close floating orifice gates not used | See MNA WA&OR_FishLadder_Condition Assessment.pdf
McNary | 7 | Oregon Fishway | Replace diffuser gratings and grate supports | See MNA WA&OR_FishLadder_Condition Assessment.pdf
McNary | 8 | Spillway | Add hoists to spillbays 2 and 19 | Spillbays 2 and 19 do not contain hoists and can only be operated using two spillway cranes.
McNary | 9 | Spillway | Rehabe/replace spillway cranes 6&7 | Cranes 6&7 underrated for lifting requirements and often OOS for repairs because of age and condition
McNary | 10 | JFF | Replace outfall sprinklers | Sprinklers and supply line lost during high flows in 2018
McNary | 11 | JFF | Add tailrace bird wires
All | 12 | Bypass system | Critical spare parts | Lack of sufficient spare parts required juvenile passage to be in emergency bypass March 2021
All | 13 | Fishways | Support for fishway temperature monitoring | CRIFM funds were provided for installation of temperature sensors that provide real-time posting of fishway temperatures but no funding has been identified for continued O&M.
Ice Harbor | 1 | Powerhouse deck | Repair/replace trash rake | Failed inspection spring 2021
Ice Harbor | 2 | South fishway | AWS pump rehab | Aging pumps have high risk of failure
Ice Harbor | 3 | North fishway | Entrance weir and hoists and controls replacement | Hoists have failed causing fishway to be temporarily closed and out of criteria
Ice Harbor | 4 | Fishways | Replace missing/broken depth gauages
Ice Harbor | 5 | Fishway | Shad exclusion/deterrent devise | Reduce adult shad passing Ice Harbor Dam, potentially reducing shad population in the Snake River
Ice Harbor | 6 | Forebay | Ladder exit debris booms | Current log booms are old and are prone to failure with east winds
Ice Harbor | 7 | Juvenile fish channel | Expansion of air burst cleaning system under inclined screen | Material purchase needed to keep screens clear of debris
Ice Harbor | 8 | Fish count station | Air motors for window brushes | $2500 per motor
Ice Harbor | 9 | Juvenile fish channel | Spare actuator for water regulating weirs
L Monumental | 1 | JFF | Hoist system for tailrace tail screens | Current system is insufficient and unsafe to operate
L Monumental | 2 | JFF | Primary Dewaterer repairs | Worn brass nuts, missing motor, weir held in place with chain
L Monumental | 3 | Forebay | Install shear boom to move debris to spillway | Debris can enter juvenile bypass system, risking injury and mortality to juvenile salmonids
L Monumental | 4 | Fishway | Fishway cooling system | Analysis shows potential to cool fishways 1-4 degrees F during warm water periods using structures similar to those installed at Little Goose and Lower Granite dams
L Monumental | 5 | Fishway | Repair /replace expansion joint seals | Leaks from fishway create saftey risks, particularily during cold weather when ice forms on walkways
L Goose | 1 | Forebay | Repair debris boom | Ineffective design collects debris and allows debris to reach powerhouse where it increases risk of injury and mortality for juvenile fish
L Goose | 2 | North shore | Replace north shore jetty | Lost during high flows, protects north shore fishway entrance from shore eddy
L Goose | 3 | Fishway | Re-design fish count station | Turbulence interferes with accurate fish counting
L Goose | 4 | Fishway | Repair /replace expansion joint seals | Leaks from fishway create saftey risks, particularily during cold weather when ice forms on walkways
L Goose | 5 | Fishway | Replace diffuser grating and support beams
L Goose | 6 | Fishway | Replace fishway control system | Fishway entrances operate in manual mode only
L Goose | 7 | Collection channel | Repair/replace corroded outer steel orifice pipe with stainless steal | Orifices have failed mid-season causing them to be closed until winter maintenance period
L Goose | 8 | Collection channel | Repair orifice valve cylinders
Lower Granite | 1 | Fishway | Modify adult trap turnpool gate | Convert to lift gate to allow fish to pass upstream without transiting the adult trap at night and weekends during passage season
Lower Granite | 2 | Fishway | Shad exclusion/ deterrent devise | Reduce adult shad in adult trap and fishway to reduce stress and crowding to salmon migrants, reduce risk from dead shad collecting on gates and screens and potentially reduce shad population upstream of Lower Granite Dam
Lower Granite | 3 | Fishway | Install/replace velocity meter in channel | Current system no working, provides inaccurate readings
Lower Granite | 4 | JFF | Complete Phase 1a modifications and resolve programing issues. | PDW/JBS
Lower Granite | 5 | Fishway | Relocate SS TW elevation sensor
Lower Granite | 6 | Fishway | Correct Control System Programing malfunction | Control system is not accurate, requiring regular inspections and manual adjustments to maintain fishway criteria
Lower Granite | 7 | Fishway | Permanently close floating orifice gates not used | Reduce leaking and annual maintenenace of stoplogs
Lower Granite | 8 | Fishway | NSE, SSE, and NPE local depth indication | Current system no working, provides inaccurate readings
Lower Granite | 9 | JFF | Shelter for truck and trailers | Maintain condition of transport equipment
Lower Granite | 10 | Barges | Improve degassing system on 2000 barges | Current pumping system is inadequate to degass river water during periods of high TDG