OFFICIAL COORDINATION REQUEST FOR

NON-ROUTINE OPERATIONS AND MAINTENANCE

COORDINATION TITLE- 21 TDA 09 MOC Fish Unit Brush Repair

COORDINATION DATE-  9 September 2021

PROJECT- The Dalles Lock & Dam

RESPONSE DATE- 23 September 2021

Description of the problem - The Dalles fish units F1 and F2 provide auxiliary water to the east fish ladder. They have been experiencing excessive brush wear which could result in damaging failure. Brush failure could result in extensive outage. They are not expected to make it to the end of this adult fish passage season. Repair will be completed as soon as possible.

Type of outage required – Fish Units 1 and 2. One unit at a time.

Impact on facility operation – F1 outage will occur Sep 28 at 0700-1400. F2 will occur Sep 29 same times. The AWS backup system will be opened immediately after each unit is off. Entrance flow will continue with one fish unit during the transition. Transition time approximately 15 minutes for open and closure each day. Total AWS flow will be reduced from 5kcfs to 2.5kcfs during that time.

Impact on unit priority - None

Impact on forebay/tailwater operation - None

Impact on spill – None.

Dates of impacts/repairs – 28 and 29 September.

Length of time for repairs – approx. 7 hours per unit, includes clearance procedures.

Analysis of potential impacts to fish

- 10-year average passage by run during the period of impact for adults and juvenile listed species, as appropriate for the proposed action and time of year;

Refer to DART or Fish Passage Center

http://www.cbr.washington.edu/dart/query/adult_daily

Table 1. Potentially impacted adults on Sept 28 and 29 (10yr avg Fish Passage Center):

| Species | Average passing 9/28 |  | Average passing 9/29 |  |
| --- | --- | --- | --- | --- |
| Fall Chinook | 4485 |  | 3844 |  |
| Steelhead | 836 |  | 189 |  |
| Unclipped Steelhead | 481 |  | 681 |  |
| Coho | 911 |  | 806 |  |
| Sockeye | 0 |  | 0 |  |

Juveniles: Very few juveniles pass the adult fishladders, and it is the tail end of the juvenile passage season.

- Statement about the current year’s run (e.g., higher or lower than 10-year average):

The NOAA forecast for adult Fall Chinook run is less than the 10 year average and the Coho run is forecast to exceed the 10 year average. Presently chinook are tracking on the 10 year and Coho about three times the 10 year average.

- Estimated exposure to impact by species and age class (i.e., number or percentage of run exposed to an impact by the action);

No impact to juvenile outmigrants, refer to table 1 for potential adult exposure.

- Type of impact by species and age class (increased delay, exposure to predation, exposure to a route of higher injury/mortality rate, exposure to higher TDG, etc.);

Potential adult passage delay could result in the 15 minute transition for open and closure AWS backup system valve. However entrance flow will not stop during this time, it will be reduced by 50%. Delay for this change is unknown.

Summary statement – Minimal passage impact is expected. Risk of long term failure outage is high. Work needs to move forward ASAP.

Downstream migrants – Depending on river flow, there might be fewer bays to pass through during the last two days of spill season. Spill volume will meet FPP

Upstream migrants (including Bull Trout)- unknown. In sufficient bull trout information available.

Lamprey – No impacts expected. Most adult lamprey passage done for season.

Comments from agencies

Final coordination results

The Corps will proceed with the work as detailed above due to the risk to fish units.

After Action update

Please email or call with questions or concerns.

Thank you,

Nathan McClain

NWP Operations Division Fishery Section (acting)

Columbia River Coordination Biologist

Nathan.A.McClain@usace.army.mil

Robert Cordie

Supervisory Fish Biologist

The Dalles Lock & Dam