# Fish Passage Plan (FPP) Change Form

Change Form # & Title:	22MCN004 – McNary Dam modified spill tables

Date Submitted:		27-Jan-22 / Updated 15-Feb-22 / REVISED 19-Apr-22

Project:  			McNary Dam

Requester Name, Agency:	Chris Peery, Corps NWW

Final Action:			APPROVED 10-Mar-22 / RESUBMITTED 19-Apr-22

FPP Section:  Spill Pattern Tables MCN-7 (with TSWs) and MCN-9 (No TSWs).

Justification for Change: Excessive wear and tear from operating beyond the designed capabilities has increased risk of failure for critical flood emergency response equipment, cranes 6 and 7. Even after extensive repairs, limiting the number of times the electrical relays for spillway cranes are operated is critical to ensure the cranes will be fully functional when needed for emergency flood situations along with spillway maintenance. The hoist for spillbay 6 is out of operation until the gearbox can be repaired.

UPDATE 19-April-2022: TSWs are surface spill spillways and pose a higher safety risk without having a means to remotely close them in an emergency. As Crane 6 does not have any remote-control capabilities, it can no longer be relied upon to operate the TSW in spillbay 19 remotely if an emergency closure is needed.  To solve this safety issue, the hoist from Spillway Bay 16 will be moved to bay 19 to allow remote controlling of the TSW and we will then move crane 6 to manually operate Spillway Bay 16 in the same manner as spillway gates 2 & 6.  The hoist for spillbay 16 is the logical choice at this time due to an initial concurrence by Ryan Laughery, that spillbay 16 would cause minimal negative impact to the spill patterns if set at a static opening as Spillway Gates 2 & 6 are.

Proposed Change:  Set the spill gates in bays 2, 6, and 16, at the locations of spillway cranes 6 and 7, to a static opening of gate step 4 or 6.  The cranes cannot be operated remotely.  If changes are required, a crane operator will be called in to adjust the gates on a limited basis.  Spillbays 6 and 16 will be set to an initial opening of step 6 during spring spill and step 4 during summer spill unless otherwise specified.

See modified spill pattern tables on the pages below.

Comments:

10-FEB-2022 FPOM:

Peery noted that the patterns should also have Bay 6 at a set opening. Wright will update the change form with the correct patterns (UPDATED 15-FEB)

FPOM asked if juvenile egress will be affected during low flow/spill with bay 6 set at 6 stops? Peery responded via email on 15-FEB: “Project biologist and Ryan Laughery did not believe this will have a significant effect on egress conditions.  Any potential effects will also be dependent on flow.  The current spill table calls for bay 6 to be open starting at spill of 100 kcfs.  In an average flow year, spill on 10 April would be closer to 150-170 kcfs with the 125% spill cap.  Biologists will be tracking tailrace conditions during the spill season and changes will be considered if determine egress conditions appear poor.”

FPOM reps need more time to discuss and refine. PENDING – will be discussed at March FPOM.

10-MAR-2022 FPOM:

Peery added that he and other NWW staff will be at the project on April 10 to observe tailrace hydraulics with this spill pattern. If problems are observed, the patterns will be re-evaluated and modified as necessary via another Change Form. APPROVED.

14-APR-2022 FPOM:

Peery provided an update that he and Laughery went to the project to observe the patterns. The tailrace looked good - there were no back eddies and flows seem to be moving downstream similar to the old pattern. A new issue has come up regarding the operation of Bay 19 with the TSW, which is currently on a crane and requires a crane crew to open/close. If there is an emergency (e.g., a boat in the BRZ), the project has no way to close the surface spill within a reasonable timeframe. It’s a significant safety issue. The project needs to move a hoist from another bay to the TSW in bay 19 so that it can be operated remotely in case of an emergency. NWW proposed moving the hoist from Bay 16 to Bay 19, which would allow the TSW in Bay 19 to be operated remotely and would set Bay 16 to a fixed number of openings like bays 2 and 6.

Record of Final Action:

APPROVED at FPOM on March 10, 2022.

RESUBMITTED April 19, 2022. Revised patterns with Bay 16 locked at four or six stops. Pending review at the May FPOM meeting.

Table MCN-7. McNary Dam Spill Patterns for Fish Passage with TSWs in Bays 19-20 and Bays 2, 6, and 16 Locked at 4 or 6 Stops.

| Table MCN-7 Spill Patterns with TSWs (# Gate Stops per Spillbay) - Bay 2, 6, and 16 locked at 4 or 6 stops |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total Stops | Spill a |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 b | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 c | 20 c | 21 | 22 b | (#) | (kcfs) |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TSW | TSW | 1 | 0 | 1 | 21.2 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | TSW | TSW | 1 | 0 | 2 | 23.2 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | TSW | TSW | 1 | 1 | 3 | 25.2 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | TSW | TSW | 2 | 1 | 4 | 27.1 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | TSW | TSW | 2 | 1 | 5 | 29.0 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | TSW | TSW | 2 | 1 | 6 | 31.0 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | TSW | TSW | 2 | 1 | 7 | 32.9 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 2 | TSW | TSW | 2 | 1 | 8 | 34.9 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 2 | TSW | TSW | 2 | 2 | 9 | 36.8 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 2 | TSW | TSW | 2 | 2 | 10 | 38.7 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 2 | 2 | TSW | TSW | 2 | 2 | 11 | 40.7 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | TSW | TSW | 2 | 2 | 12 | 42.6 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | TSW | TSW | 2 | 2 | 13 | 44.6 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | TSW | TSW | 2 | 2 | 14 | 46.5 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 15 | 47.9 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 16 | 49.8 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 17 | 51.8 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 18 | 53.7 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 19 | 55.7 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 20 | 57.6 |
| 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 21 | 59.6 |
| 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 22 | 61.5 |
| 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 23 | 63.5 |
| 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 24 | 65.4 |
| 0 | 0 | 2 | 0 | 2 | 0 | 1 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 25 | 67.4 |
| 0 | 4 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 26 | 68.7 |
| 0 | 4 | 0 | 0 | 2 | 0 | 1 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 27 | 70.7 |
| 0 | 4 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 28 | 72.6 |
| 0 | 4 | 1 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 29 | 74.6 |
| 0 | 4 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 30 | 76.5 |
| 1 | 4 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 31 | 78.5 |
| 2 | 4 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 32 | 80.4 |
| 2 | 4 | 2 | 1 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 33 | 82.4 |
| 2 | 4 | 2 | 2 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 34 | 84.3 |
| 2 | 4 | 2 | 2 | 2 | 0 | 2 | 1 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 35 | 86.3 |
| 2 | 4 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 36 | 88.2 |
| 2 | 4 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 0 | 2 | 1 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 37 | 90.2 |
| 2 | 4 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 38 | 92.1 |
| 2 | 4 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 39 | 94.1 |
| 2 | 4 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 40 | 96.0 |
| 2 | 4 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 41 | 98.0 |
| 2 | 4 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 42 | 99.9 |
| 2 | 4 | 2 | 2 | 3 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 43 | 101.6 |
| 2 | 4 | 2 | 2 | 0 | 6 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 44 | 102.5 |
| 2 | 4 | 2 | 2 | 0 | 6 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 45 | 104.5 |
| 2 | 4 | 2 | 2 | 0 | 6 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 46 | 106.4 |
| 2 | 4 | 2 | 2 | 1 | 6 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 47 | 108.4 |
| 2 | 4 | 2 | 2 | 2 | 6 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | TSW | TSW | 2 | 2 | 48 | 110.3 |
| 2 | 4 | 2 | 2 | 2 | 6 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | TSW | TSW | 3 | 2 | 49 | 112.0 |
| 2 | 4 | 2 | 2 | 2 | 6 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 3 | TSW | TSW | 3 | 2 | 50 | 113.7 |
| 2 | 4 | 3 | 2 | 2 | 6 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 3 | TSW | TSW | 3 | 2 | 51 | 115.4 |
| 2 | 4 | 3 | 2 | 3 | 6 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 3 | TSW | TSW | 3 | 2 | 52 | 117.1 |
| 2 | 4 | 3 | 2 | 3 | 6 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 4 | 2 | 3 | TSW | TSW | 3 | 2 | 53 | 118.8 |
| 2 | 4 | 3 | 2 | 3 | 6 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 4 | 2 | 3 | TSW | TSW | 3 | 2 | 54 | 120.5 |
| 2 | 4 | 3 | 2 | 3 | 6 | 3 | 2 | 2 | 2 | 2 | 3 | 2 | 3 | 2 | 4 | 2 | 3 | TSW | TSW | 3 | 2 | 55 | 122.2 |
| 2 | 4 | 3 | 2 | 3 | 6 | 3 | 2 | 3 | 2 | 2 | 3 | 2 | 3 | 2 | 4 | 2 | 3 | TSW | TSW | 3 | 2 | 56 | 123.9 |
| 2 | 4 | 3 | 2 | 3 | 6 | 3 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 2 | 4 | 2 | 3 | TSW | TSW | 3 | 2 | 57 | 125.6 |
| 2 | 4 | 3 | 2 | 3 | 6 | 3 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 2 | 4 | 2 | 3 | TSW | TSW | 3 | 3 | 58 | 127.3 |
| 3 | 4 | 3 | 2 | 3 | 6 | 3 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 2 | 4 | 2 | 3 | TSW | TSW | 3 | 3 | 59 | 129.0 |
| 3 | 4 | 3 | 2 | 3 | 6 | 3 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 2 | 4 | 3 | 3 | TSW | TSW | 3 | 3 | 60 | 130.7 |
| 3 | 4 | 3 | 3 | 3 | 6 | 3 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 2 | 4 | 3 | 3 | TSW | TSW | 3 | 3 | 61 | 132.4 |
| 3 | 4 | 3 | 3 | 3 | 6 | 3 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 3 | 4 | 3 | 3 | TSW | TSW | 3 | 3 | 62 | 134.1 |
| 3 | 4 | 3 | 3 | 3 | 6 | 3 | 3 | 3 | 3 | 2 | 3 | 2 | 3 | 3 | 4 | 3 | 3 | TSW | TSW | 3 | 3 | 63 | 135.8 |
| 3 | 4 | 3 | 3 | 3 | 6 | 3 | 3 | 3 | 3 | 2 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | TSW | TSW | 3 | 3 | 64 | 137.5 |
| 3 | 4 | 3 | 3 | 3 | 6 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | TSW | TSW | 3 | 3 | 65 | 139.2 |
| 3 | 4 | 3 | 3 | 3 | 6 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | TSW | TSW | 4 | 3 | 66 | 140.8 |
| 3 | 4 | 3 | 3 | 3 | 6 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 4 | TSW | TSW | 4 | 3 | 67 | 142.4 |
| 3 | 4 | 4 | 3 | 3 | 6 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 4 | TSW | TSW | 4 | 3 | 68 | 144.0 |
| 3 | 4 | 4 | 3 | 4 | 6 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 4 | TSW | TSW | 4 | 3 | 69 | 145.6 |
| 3 | 4 | 4 | 3 | 4 | 6 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 4 | 3 | 4 | TSW | TSW | 4 | 3 | 70 | 147.2 |
| 3 | 4 | 4 | 3 | 4 | 6 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 4 | 3 | 4 | TSW | TSW | 4 | 3 | 71 | 148.8 |
| 3 | 4 | 4 | 3 | 4 | 6 | 4 | 3 | 3 | 3 | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | TSW | TSW | 4 | 3 | 72 | 150.4 |
| 3 | 4 | 4 | 3 | 4 | 6 | 4 | 3 | 4 | 3 | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | TSW | TSW | 4 | 3 | 73 | 152.0 |
| 3 | 4 | 4 | 3 | 4 | 6 | 4 | 3 | 4 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | TSW | TSW | 4 | 3 | 74 | 153.6 |
| 3 | 4 | 4 | 3 | 4 | 6 | 4 | 3 | 4 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | TSW | TSW | 4 | 4 | 75 | 155.2 |
| 4 | 4 | 4 | 3 | 4 | 6 | 4 | 3 | 4 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | TSW | TSW | 4 | 4 | 76 | 156.8 |
| 4 | 4 | 4 | 3 | 4 | 6 | 4 | 3 | 4 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | 4 | 4 | TSW | TSW | 4 | 4 | 77 | 158.4 |
| 4 | 4 | 4 | 4 | 4 | 6 | 4 | 3 | 4 | 4 | 3 | 4 | 3 | 4 | 3 | 4 | 4 | 4 | TSW | TSW | 4 | 4 | 78 | 160.0 |
| 4 | 4 | 4 | 4 | 4 | 6 | 4 | 3 | 4 | 4 | 3 | 4 | 3 | 4 | 4 | 4 | 4 | 4 | TSW | TSW | 4 | 4 | 79 | 161.6 |
| 4 | 4 | 4 | 4 | 4 | 6 | 4 | 4 | 4 | 4 | 3 | 4 | 3 | 4 | 4 | 4 | 4 | 4 | TSW | TSW | 4 | 4 | 80 | 163.2 |
| 4 | 4 | 4 | 4 | 4 | 6 | 4 | 4 | 4 | 4 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | TSW | TSW | 4 | 4 | 81 | 164.8 |
| 4 | 4 | 4 | 4 | 4 | 6 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | TSW | TSW | 4 | 4 | 82 | 166.4 |
| 4 | 4 | 4 | 4 | 4 | 6 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | TSW | TSW | 5 | 4 | 83 | 168.0 |
| 4 | 4 | 4 | 4 | 4 | 6 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | TSW | TSW | 5 | 4 | 84 | 169.6 |
| 4 | 4 | 5 | 4 | 4 | 6 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | TSW | TSW | 5 | 4 | 85 | 171.2 |
| 4 | 4 | 5 | 4 | 5 | 6 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | TSW | TSW | 5 | 4 | 86 | 172.8 |
| 4 | 4 | 5 | 4 | 5 | 6 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 4 | 5 | TSW | TSW | 5 | 4 | 87 | 174.4 |
| 4 | 4 | 5 | 4 | 5 | 6 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 4 | 5 | TSW | TSW | 5 | 4 | 88 | 176.0 |
| 4 | 4 | 5 | 4 | 5 | 6 | 5 | 4 | 4 | 4 | 4 | 5 | 4 | 5 | 4 | 4 | 4 | 5 | TSW | TSW | 5 | 4 | 89 | 177.6 |
| 4 | 4 | 5 | 4 | 5 | 6 | 5 | 4 | 5 | 4 | 4 | 5 | 4 | 5 | 4 | 4 | 4 | 5 | TSW | TSW | 5 | 4 | 90 | 179.2 |
| 4 | 4 | 5 | 4 | 5 | 6 | 5 | 4 | 5 | 5 | 4 | 5 | 4 | 5 | 4 | 4 | 4 | 5 | TSW | TSW | 5 | 4 | 91 | 180.8 |
| 4 | 4 | 5 | 4 | 5 | 6 | 5 | 4 | 5 | 5 | 4 | 5 | 4 | 5 | 4 | 4 | 4 | 5 | TSW | TSW | 5 | 5 | 92 | 182.4 |
| 5 | 4 | 5 | 4 | 5 | 6 | 5 | 4 | 5 | 5 | 4 | 5 | 4 | 5 | 4 | 4 | 4 | 5 | TSW | TSW | 5 | 5 | 93 | 184.0 |
| 5 | 4 | 5 | 4 | 5 | 6 | 5 | 4 | 5 | 5 | 4 | 5 | 4 | 5 | 4 | 4 | 5 | 5 | TSW | TSW | 5 | 5 | 94 | 185.6 |
| 5 | 4 | 5 | 5 | 5 | 6 | 5 | 4 | 5 | 5 | 4 | 5 | 4 | 5 | 4 | 4 | 5 | 5 | TSW | TSW | 5 | 5 | 95 | 187.2 |
| 5 | 4 | 5 | 5 | 5 | 6 | 5 | 4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4 | 5 | 5 | TSW | TSW | 5 | 5 | 96 | 188.8 |
| 5 | 4 | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4 | 5 | 5 | TSW | TSW | 5 | 5 | 97 | 190.4 |
| 5 | 4 | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | TSW | TSW | 5 | 5 | 98 | 192.0 |
| 5 | 4 | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | TSW | TSW | 5 | 5 | 99 | 193.6 |
| 5 | 4 | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | TSW | TSW | 6 | 5 | 100 | 195.2 |
| 5 | 4 | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 6 | TSW | TSW | 6 | 5 | 101 | 196.8 |
| 5 | 4 | 6 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 6 | TSW | TSW | 6 | 5 | 102 | 198.4 |
| 5 | 4 | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 6 | TSW | TSW | 6 | 5 | 103 | 200.0 |
| 5 | 4 | 6 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 6 | TSW | TSW | 6 | 5 | 104 | 201.6 |
| 5 | 4 | 6 | 5 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 6 | TSW | TSW | 6 | 5 | 105 | 203.2 |
| 5 | 4 | 6 | 5 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 6 | 5 | 6 | TSW | TSW | 6 | 5 | 106 | 204.8 |
| 5 | 4 | 6 | 5 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 6 | 5 | 6 | TSW | TSW | 6 | 5 | 107 | 206.4 |
| 5 | 4 | 6 | 5 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | TSW | TSW | 6 | 5 | 108 | 208.0 |
| 5 | 4 | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 5 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | TSW | TSW | 6 | 5 | 109 | 209.6 |
| 5 | 4 | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | TSW | TSW | 6 | 5 | 110 | 211.2 |
| 5 | 4 | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | TSW | TSW | 6 | 6 | 111 | 212.8 |
| 6 | 4 | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | TSW | TSW | 6 | 6 | 112 | 214.4 |
| 6 | 4 | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 6 | 6 | TSW | TSW | 6 | 6 | 113 | 216.0 |
| 6 | 4 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 6 | 6 | TSW | TSW | 6 | 6 | 114 | 217.6 |
| 6 | 4 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | TSW | TSW | 6 | 6 | 115 | 219.2 |
| 6 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | TSW | TSW | 6 | 6 | 116 | 220.8 |
| 6 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | TSW | TSW | 6 | 6 | 117 | 222.4 |
| 6 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | TSW | TSW | 6 | 6 | 118 | 224.0 |
| 6 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | TSW | TSW | 7 | 6 | 119 | 225.6 |
| 6 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | TSW | TSW | 7 | 6 | 120 | 227.2 |
| 6 | 4 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | TSW | TSW | 7 | 6 | 121 | 228.8 |
| 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | TSW | TSW | 7 | 6 | 122 | 230.4 |
| 6 | 6 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | TSW | TSW | 7 | 6 | 123 | 232.0 |
| 6 | 6 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | TSW | TSW | 7 | 6 | 125 | 235.2 |
| 6 | 6 | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | TSW | TSW | 7 | 6 | 126 | 236.8 |
| 6 | 6 | 7 | 7 | 7 | 6 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 6 | 7 | 7 | TSW | TSW | 7 | 6 | 128 | 240.0 |
| 6 | 6 | 7 | 7 | 7 | 6 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 6 | 7 | 7 | TSW | TSW | 7 | 6 | 130 | 243.2 |
| 6 | 6 | 7 | 7 | 7 | 6 | 7 | 7 | 7 | 6 | 6 | 6 | 7 | 7 | 7 | 6 | 7 | 7 | TSW | TSW | 7 | 6 | 132 | 246.4 |
| 6 | 6 | 7 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 6 | 7 | 7 | TSW | TSW | 7 | 6 | 134 | 249.6 |
| 7 | 6 | 7 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 7 | TSW | TSW | 7 | 6 | 136 | 252.8 |
| 7 | 6 | 7 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 8 | TSW | TSW | 7 | 7 | 138 | 256.1 |
| 7 | 6 | 8 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 8 | TSW | TSW | 8 | 7 | 140 | 259.5 |
| 7 | 6 | 8 | 8 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 8 | 8 | TSW | TSW | 8 | 7 | 142 | 262.9 |
| 7 | 6 | 8 | 8 | 8 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 8 | 8 | TSW | TSW | 8 | 7 | 143 | 264.6 |
| 7 | 6 | 8 | 8 | 8 | 6 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 6 | 8 | 8 | TSW | TSW | 8 | 7 | 145 | 268.0 |
| 7 | 6 | 8 | 8 | 8 | 6 | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 6 | 8 | 8 | TSW | TSW | 8 | 7 | 147 | 271.4 |
| 7 | 6 | 8 | 8 | 8 | 6 | 8 | 8 | 8 | 7 | 7 | 7 | 8 | 8 | 8 | 6 | 8 | 8 | TSW | TSW | 8 | 7 | 149 | 274.8 |
| 7 | 6 | 8 | 8 | 8 | 6 | 8 | 8 | 8 | 8 | 7 | 8 | 8 | 8 | 8 | 6 | 8 | 8 | TSW | TSW | 8 | 7 | 151 | 278.2 |
| 8 | 6 | 8 | 8 | 8 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 8 | 8 | TSW | TSW | 8 | 7 | 153 | 281.6 |
| 8 | 6 | 8 | 8 | 8 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 8 | 9 | TSW | TSW | 8 | 8 | 155 | 284.9 |
| 8 | 6 | 9 | 8 | 8 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 8 | 9 | TSW | TSW | 9 | 8 | 157 | 288.1 |
| 8 | 6 | 9 | 9 | 8 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 9 | 9 | TSW | TSW | 9 | 8 | 159 | 291.3 |
| 8 | 6 | 9 | 9 | 9 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 9 | 9 | TSW | TSW | 9 | 8 | 160 | 292.9 |
| 8 | 6 | 9 | 9 | 9 | 6 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 6 | 9 | 9 | TSW | TSW | 9 | 8 | 162 | 296.1 |
| 8 | 6 | 9 | 9 | 9 | 6 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 6 | 9 | 9 | TSW | TSW | 9 | 8 | 164 | 299.3 |
| 8 | 6 | 9 | 9 | 9 | 6 | 9 | 9 | 9 | 8 | 8 | 8 | 9 | 9 | 9 | 6 | 9 | 9 | TSW | TSW | 9 | 8 | 166 | 302.5 |
| 8 | 6 | 9 | 9 | 9 | 6 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 9 | 6 | 9 | 9 | TSW | TSW | 9 | 8 | 168 | 305.7 |
| 9 | 6 | 9 | 9 | 9 | 6 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 9 | 9 | TSW | TSW | 9 | 8 | 170 | 308.9 |
| 9 | 6 | 9 | 9 | 9 | 6 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 9 | 10 | TSW | TSW | 9 | 9 | 172 | 312.1 |
| 9 | 6 | 10 | 9 | 9 | 6 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 9 | 10 | TSW | TSW | 10 | 9 | 174 | 315.3 |
| 9 | 6 | 10 | 10 | 9 | 6 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 10 | 10 | TSW | TSW | 10 | 9 | 176 | 318.5 |
| 9 | 6 | 10 | 10 | 10 | 6 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 10 | 10 | TSW | TSW | 10 | 9 | 177 | 320.1 |
| 9 | 6 | 10 | 10 | 10 | 6 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 6 | 10 | 10 | TSW | TSW | 10 | 9 | 179 | 323.3 |
| 9 | 6 | 10 | 10 | 10 | 6 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 6 | 10 | 10 | TSW | TSW | 10 | 9 | 181 | 326.5 |
| 9 | 6 | 10 | 10 | 10 | 6 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 6 | 10 | 10 | TSW | TSW | 10 | 9 | 183 | 329.7 |
| 9 | 6 | 10 | 10 | 10 | 6 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 6 | 10 | 10 | TSW | TSW | 10 | 9 | 185 | 332.9 |
| 10 | 6 | 10 | 10 | 10 | 6 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 6 | 10 | 10 | TSW | TSW | 10 | 9 | 187 | 336.1 |
| 10 | 6 | 10 | 10 | 10 | 6 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 6 | 10 | 11 | TSW | TSW | 10 | 10 | 189 | 339.2 |
| 10 | 6 | 11 | 10 | 10 | 6 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 6 | 10 | 11 | TSW | TSW | 11 | 10 | 191 | 342.2 |
| 10 | 6 | 11 | 11 | 10 | 6 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 6 | 11 | 11 | TSW | TSW | 11 | 10 | 193 | 345.2 |
| 10 | 6 | 11 | 11 | 11 | 6 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 6 | 11 | 11 | TSW | TSW | 11 | 10 | 194 | 346.7 |
| 10 | 6 | 11 | 11 | 11 | 6 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 6 | 11 | 11 | TSW | TSW | 11 | 10 | 196 | 349.7 |
| 10 | 6 | 11 | 11 | 11 | 6 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 6 | 11 | 11 | TSW | TSW | 11 | 10 | 198 | 352.7 |
| 10 | 6 | 11 | 11 | 11 | 6 | 11 | 11 | 11 | 10 | 10 | 10 | 11 | 11 | 11 | 6 | 11 | 11 | TSW | TSW | 11 | 10 | 200 | 355.7 |
| 10 | 6 | 11 | 11 | 11 | 6 | 11 | 11 | 11 | 11 | 10 | 11 | 11 | 11 | 11 | 6 | 11 | 11 | TSW | TSW | 11 | 10 | 202 | 358.7 |
| 11 | 6 | 11 | 11 | 11 | 6 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 6 | 11 | 11 | TSW | TSW | 11 | 10 | 204 | 361.7 |
| 11 | 6 | 11 | 11 | 11 | 6 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 6 | 11 | 12 | TSW | TSW | 11 | 11 | 206 | 364.8 |
| 11 | 6 | 12 | 11 | 11 | 6 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 6 | 11 | 12 | TSW | TSW | 12 | 11 | 208 | 368.0 |
| 11 | 6 | 12 | 12 | 11 | 6 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 6 | 12 | 12 | TSW | TSW | 12 | 11 | 210 | 371.2 |
| 11 | 6 | 12 | 12 | 12 | 6 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 6 | 12 | 12 | TSW | TSW | 12 | 11 | 211 | 372.8 |
| 11 | 6 | 12 | 12 | 12 | 6 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 6 | 12 | 12 | TSW | TSW | 12 | 11 | 213 | 376.0 |
| 11 | 6 | 12 | 12 | 12 | 6 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 6 | 12 | 12 | TSW | TSW | 12 | 11 | 215 | 379.2 |
| 11 | 6 | 12 | 12 | 12 | 6 | 12 | 12 | 12 | 11 | 11 | 11 | 12 | 12 | 12 | 6 | 12 | 12 | TSW | TSW | 12 | 11 | 217 | 382.4 |
| 11 | 6 | 12 | 12 | 12 | 6 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 12 | 12 | 6 | 12 | 12 | TSW | TSW | 12 | 11 | 219 | 385.6 |
| 12 | 6 | 12 | 12 | 12 | 6 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 12 | 12 | TSW | TSW | 12 | 11 | 221 | 388.8 |
| 12 | 6 | 12 | 12 | 12 | 6 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 12 | 13 | TSW | TSW | 12 | 12 | 223 | 392.0 |
| 12 | 6 | 13 | 12 | 12 | 6 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 12 | 13 | TSW | TSW | 13 | 12 | 225 | 395.2 |
| 12 | 6 | 13 | 13 | 12 | 6 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 13 | 13 | TSW | TSW | 13 | 12 | 227 | 398.4 |
| 12 | 6 | 13 | 13 | 13 | 6 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 13 | 13 | TSW | TSW | 13 | 12 | 228 | 400.0 |
| 12 | 6 | 13 | 13 | 13 | 6 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 6 | 13 | 13 | TSW | TSW | 13 | 12 | 230 | 403.2 |
| 12 | 6 | 13 | 13 | 13 | 6 | 13 | 13 | 12 | 12 | 12 | 12 | 12 | 13 | 13 | 6 | 13 | 13 | TSW | TSW | 13 | 12 | 232 | 406.4 |
| 12 | 6 | 13 | 13 | 13 | 6 | 13 | 13 | 13 | 12 | 12 | 12 | 13 | 13 | 13 | 6 | 13 | 13 | TSW | TSW | 13 | 12 | 234 | 409.6 |
| 12 | 6 | 13 | 13 | 13 | 6 | 13 | 13 | 13 | 13 | 12 | 13 | 13 | 13 | 13 | 6 | 13 | 13 | TSW | TSW | 13 | 12 | 236 | 412.8 |
| 12 | 6 | 13 | 13 | 13 | 6 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 6 | 13 | 13 | TSW | TSW | 13 | 12 | 237 | 414.4 |
| 13 | 6 | 13 | 13 | 13 | 6 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 6 | 13 | 13 | TSW | TSW | 13 | 13 | 239 | 417.6 |

Table MCN-9. McNary Dam Spill Patterns with No TSWs and Bays 2, 6, and 16 Locked at 4 or 6 Stops.

| Table MCN-9 Spill Patterns with No TSWs (# Gate Stops per Spillbay) - Bays 2, 6 & 16 locked at 4 or 6 stops. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total Stops | Spill a |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 b | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 b | (#) | (kcfs) |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 5.6 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 4 | 7.2 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 0 | 5 | 9.5 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 0 | 0 | 0 | 6 | 11.1 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 2 | 0 | 0 | 7 | 13.4 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 8 | 15.0 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 9 | 17.0 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 10 | 18.9 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 11 | 20.9 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 12 | 22.8 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 13 | 24.8 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 14 | 26.7 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 15 | 28.7 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 16 | 30.6 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 17 | 32.6 |
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 18 | 34.5 |
| 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 19 | 36.5 |
| 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 20 | 38.4 |
| 0 | 0 | 1 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 21 | 40.4 |
| 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 2 | 0 | 0 | 22 | 42.3 |
| 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 2 | 1 | 0 | 23 | 44.3 |
| 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 2 | 2 | 0 | 24 | 46.2 |
| 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 3 | 2 | 0 | 25 | 47.9 |
| 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 4 | 2 | 0 | 26 | 49.5 |
| 1 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 4 | 2 | 0 | 27 | 51.5 |
| 2 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 4 | 2 | 0 | 28 | 53.4 |
| 3 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 4 | 2 | 0 | 29 | 55.1 |
| 0 | 4 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 4 | 2 | 0 | 30 | 56.7 |
| 0 | 4 | 3 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 4 | 2 | 0 | 31 | 58.4 |
| 0 | 4 | 4 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 4 | 2 | 0 | 32 | 60.0 |
| 0 | 4 | 4 | 0 | 2 | 0 | 1 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 4 | 2 | 0 | 33 | 62.0 |
| 0 | 4 | 4 | 0 | 2 | 0 | 2 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 4 | 2 | 0 | 34 | 63.9 |
| 0 | 4 | 4 | 0 | 2 | 0 | 3 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 4 | 2 | 0 | 35 | 65.6 |
| 0 | 4 | 4 | 0 | 2 | 4 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 2 | 4 | 4 | 2 | 0 | 36 | 67.2 |
| 0 | 4 | 4 | 0 | 2 | 4 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 1 | 2 | 4 | 4 | 2 | 0 | 37 | 69.2 |
| 0 | 4 | 4 | 0 | 2 | 4 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 4 | 4 | 2 | 0 | 38 | 71.1 |
| 0 | 4 | 4 | 0 | 2 | 4 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 3 | 2 | 4 | 4 | 2 | 0 | 39 | 72.8 |
| 0 | 4 | 4 | 0 | 2 | 4 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 4 | 0 | 2 | 4 | 4 | 2 | 0 | 40 | 74.4 |
| 0 | 4 | 4 | 0 | 2 | 4 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 4 | 1 | 2 | 4 | 4 | 2 | 0 | 41 | 76.4 |
| 0 | 4 | 4 | 0 | 2 | 4 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 0 | 42 | 78.3 |
| 1 | 4 | 4 | 0 | 2 | 4 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 0 | 43 | 80.3 |
| 2 | 4 | 4 | 0 | 2 | 4 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 0 | 44 | 82.2 |
| 2 | 4 | 4 | 1 | 2 | 4 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 0 | 45 | 84.2 |
| 2 | 4 | 4 | 2 | 2 | 4 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 0 | 46 | 86.1 |
| 2 | 4 | 4 | 2 | 2 | 4 | 1 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 0 | 47 | 88.1 |
| 2 | 4 | 4 | 2 | 2 | 4 | 2 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 0 | 48 | 90.0 |
| 2 | 4 | 4 | 2 | 2 | 4 | 2 | 2 | 1 | 2 | 0 | 2 | 0 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 0 | 49 | 92.0 |
| 2 | 4 | 4 | 2 | 2 | 4 | 2 | 2 | 2 | 2 | 0 | 2 | 0 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 0 | 50 | 93.9 |
| 2 | 4 | 4 | 2 | 2 | 4 | 2 | 2 | 2 | 2 | 1 | 2 | 0 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 0 | 51 | 95.9 |
| 2 | 4 | 4 | 2 | 2 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 0 | 52 | 97.8 |
| 2 | 4 | 4 | 2 | 2 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 0 | 53 | 99.8 |
| 2 | 4 | 4 | 2 | 2 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 0 | 54 | 101.7 |
| 2 | 4 | 4 | 2 | 2 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 1 | 55 | 103.7 |
| 2 | 4 | 4 | 2 | 2 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | 4 | 4 | 2 | 2 | 56 | 105.6 |
| 2 | 4 | 4 | 2 | 2 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | 5 | 4 | 2 | 2 | 57 | 107.2 |
| 2 | 4 | 4 | 2 | 2 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | 5 | 5 | 2 | 2 | 58 | 108.8 |
| 2 | 4 | 4 | 2 | 2 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 3 | 5 | 5 | 2 | 2 | 59 | 110.5 |
| 2 | 4 | 4 | 2 | 2 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 3 | 5 | 5 | 3 | 2 | 60 | 112.2 |
| 2 | 4 | 4 | 3 | 2 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 3 | 5 | 5 | 3 | 2 | 61 | 113.9 |
| 2 | 4 | 4 | 3 | 2 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 3 | 3 | 5 | 5 | 3 | 2 | 62 | 115.6 |
| 2 | 4 | 4 | 3 | 3 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 3 | 3 | 5 | 5 | 3 | 2 | 63 | 117.3 |
| 2 | 4 | 4 | 3 | 3 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 3 | 3 | 5 | 5 | 3 | 2 | 64 | 119.0 |
| 2 | 4 | 4 | 3 | 3 | 4 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 3 | 3 | 5 | 5 | 3 | 2 | 65 | 120.7 |
| 2 | 4 | 4 | 3 | 3 | 4 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 4 | 3 | 3 | 5 | 5 | 3 | 2 | 66 | 122.4 |
| 2 | 4 | 4 | 3 | 3 | 4 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 4 | 3 | 3 | 5 | 5 | 3 | 2 | 67 | 124.1 |
| 2 | 4 | 4 | 3 | 3 | 4 | 3 | 3 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 3 | 3 | 5 | 5 | 3 | 2 | 68 | 125.8 |
| 2 | 4 | 4 | 3 | 3 | 4 | 3 | 3 | 3 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 3 | 3 | 5 | 5 | 3 | 2 | 69 | 127.5 |
| 2 | 4 | 4 | 3 | 3 | 4 | 3 | 3 | 3 | 2 | 2 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 5 | 5 | 3 | 2 | 70 | 129.2 |
| 2 | 4 | 4 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 2 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 5 | 5 | 3 | 2 | 71 | 130.9 |
| 2 | 4 | 4 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 5 | 5 | 3 | 2 | 72 | 132.6 |
| 3 | 4 | 4 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 5 | 5 | 3 | 2 | 73 | 134.3 |
| 3 | 4 | 4 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 5 | 5 | 3 | 3 | 74 | 136.0 |
| 3 | 4 | 5 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 5 | 5 | 3 | 3 | 75 | 137.6 |
| 3 | 4 | 5 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 6 | 5 | 3 | 3 | 76 | 139.2 |
| 3 | 4 | 5 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 6 | 6 | 3 | 3 | 77 | 140.8 |
| 3 | 4 | 5 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 4 | 6 | 6 | 3 | 3 | 78 | 142.4 |
| 3 | 4 | 5 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 4 | 6 | 6 | 4 | 3 | 79 | 144.0 |
| 3 | 4 | 5 | 4 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 4 | 6 | 6 | 4 | 3 | 80 | 145.6 |
| 3 | 4 | 5 | 4 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 6 | 4 | 3 | 81 | 147.2 |
| 3 | 4 | 5 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 6 | 4 | 3 | 82 | 148.8 |
| 3 | 4 | 5 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 6 | 6 | 4 | 3 | 83 | 150.4 |
| 3 | 4 | 5 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 6 | 6 | 4 | 3 | 84 | 152.0 |
| 3 | 4 | 5 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 6 | 6 | 4 | 3 | 85 | 153.6 |
| 3 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 6 | 6 | 4 | 3 | 86 | 155.2 |
| 3 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 6 | 6 | 4 | 3 | 87 | 156.8 |
| 3 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 6 | 6 | 4 | 3 | 88 | 158.4 |
| 3 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 6 | 6 | 4 | 3 | 89 | 160.0 |
| 3 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 6 | 6 | 4 | 3 | 90 | 161.6 |
| 3 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 6 | 6 | 4 | 3 | 91 | 163.2 |
| 4 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 6 | 6 | 4 | 3 | 92 | 164.8 |
| 4 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 6 | 6 | 4 | 4 | 93 | 166.4 |
| 4 | 4 | 6 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 6 | 6 | 4 | 4 | 94 | 168.0 |
| 4 | 4 | 6 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 7 | 6 | 4 | 4 | 95 | 169.6 |
| 4 | 4 | 6 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 7 | 7 | 4 | 4 | 96 | 171.2 |
| 4 | 4 | 6 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 7 | 7 | 4 | 4 | 97 | 172.8 |
| 4 | 4 | 6 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 7 | 7 | 5 | 4 | 98 | 174.4 |
| 4 | 4 | 6 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 7 | 7 | 5 | 4 | 99 | 176.0 |
| 4 | 4 | 6 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 7 | 7 | 5 | 4 | 100 | 177.6 |
| 4 | 4 | 6 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 7 | 7 | 5 | 4 | 101 | 179.2 |
| 4 | 4 | 6 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 5 | 5 | 7 | 7 | 5 | 4 | 102 | 180.8 |
| 4 | 4 | 6 | 5 | 5 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 5 | 5 | 7 | 7 | 5 | 4 | 103 | 182.4 |
| 4 | 4 | 6 | 5 | 5 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 4 | 5 | 5 | 7 | 7 | 5 | 4 | 104 | 184.0 |
| 4 | 4 | 6 | 5 | 5 | 4 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 4 | 5 | 5 | 7 | 7 | 5 | 4 | 105 | 185.6 |
| 4 | 4 | 6 | 5 | 5 | 4 | 5 | 5 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 4 | 5 | 5 | 7 | 7 | 5 | 4 | 106 | 187.2 |
| 4 | 4 | 6 | 5 | 5 | 4 | 5 | 5 | 5 | 4 | 4 | 4 | 5 | 5 | 5 | 4 | 5 | 5 | 7 | 7 | 5 | 4 | 107 | 188.8 |
| 4 | 4 | 6 | 5 | 5 | 4 | 5 | 5 | 5 | 4 | 4 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 7 | 7 | 5 | 4 | 108 | 190.4 |
| 4 | 4 | 6 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 7 | 7 | 5 | 4 | 109 | 192.0 |
| 4 | 4 | 6 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 7 | 7 | 5 | 4 | 110 | 193.6 |
| 5 | 4 | 6 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 7 | 7 | 5 | 4 | 111 | 195.2 |
| 5 | 4 | 6 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 7 | 7 | 5 | 5 | 112 | 196.8 |
| 5 | 4 | 7 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 7 | 7 | 5 | 5 | 113 | 198.4 |
| 5 | 4 | 7 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 8 | 7 | 5 | 5 | 114 | 200.1 |
| 5 | 4 | 7 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 8 | 8 | 5 | 5 | 115 | 201.8 |
| 5 | 4 | 7 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 6 | 8 | 8 | 5 | 5 | 116 | 203.4 |
| 5 | 4 | 7 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 6 | 8 | 8 | 6 | 5 | 117 | 205.0 |
| 5 | 4 | 7 | 6 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 6 | 8 | 8 | 6 | 5 | 118 | 206.6 |
| 5 | 4 | 7 | 6 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 6 | 6 | 8 | 8 | 6 | 5 | 119 | 208.2 |
| 5 | 4 | 7 | 6 | 6 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 6 | 6 | 8 | 8 | 6 | 5 | 120 | 209.8 |
| 5 | 4 | 7 | 6 | 6 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 5 | 121 | 211.4 |
| 5 | 4 | 7 | 6 | 6 | 4 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 5 | 122 | 213.0 |
| 5 | 4 | 7 | 6 | 6 | 4 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 5 | 123 | 214.6 |
| 5 | 4 | 7 | 6 | 6 | 4 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 5 | 124 | 216.2 |
| 5 | 4 | 7 | 6 | 6 | 4 | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 5 | 125 | 217.8 |
| 5 | 4 | 7 | 6 | 6 | 4 | 6 | 6 | 6 | 5 | 5 | 5 | 6 | 6 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 5 | 126 | 219.4 |
| 5 | 4 | 7 | 6 | 6 | 4 | 6 | 6 | 6 | 5 | 5 | 6 | 6 | 6 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 5 | 127 | 221.0 |
| 5 | 4 | 7 | 6 | 6 | 4 | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 5 | 128 | 222.6 |
| 5 | 4 | 7 | 6 | 6 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 5 | 129 | 224.2 |
| 6 | 4 | 7 | 6 | 6 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 5 | 130 | 225.8 |
| 6 | 4 | 7 | 6 | 6 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 6 | 131 | 227.4 |
| 6 | 4 | 8 | 6 | 6 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 6 | 132 | 229.1 |
| 5 | 6 | 8 | 6 | 6 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 6 | 133 | 230.7 |
| 6 | 6 | 8 | 6 | 6 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 6 | 134 | 232.3 |
| 5 | 6 | 8 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 6 | 135 | 233.9 |
| 6 | 6 | 8 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4 | 6 | 6 | 8 | 8 | 6 | 6 | 136 | 235.5 |
| 5 | 6 | 8 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 8 | 6 | 6 | 137 | 237.1 |
| 6 | 6 | 8 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 8 | 6 | 6 | 138 | 238.7 |
| 6 | 6 | 8 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 9 | 8 | 6 | 6 | 139 | 240.3 |
| 6 | 6 | 8 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 9 | 9 | 6 | 6 | 140 | 241.9 |
| 6 | 6 | 8 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 9 | 9 | 6 | 6 | 141 | 243.5 |
| 6 | 6 | 8 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 9 | 9 | 7 | 6 | 142 | 245.1 |
| 6 | 6 | 8 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 9 | 9 | 7 | 6 | 143 | 246.7 |
| 6 | 6 | 8 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 9 | 9 | 7 | 6 | 144 | 248.3 |
| 6 | 6 | 8 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 9 | 9 | 7 | 6 | 145 | 249.9 |
| 6 | 6 | 8 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 6 | 7 | 7 | 9 | 9 | 7 | 6 | 146 | 251.5 |
| 6 | 6 | 8 | 7 | 7 | 6 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 6 | 7 | 7 | 9 | 9 | 7 | 6 | 147 | 253.1 |
| 6 | 6 | 8 | 7 | 7 | 6 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 6 | 7 | 7 | 9 | 9 | 7 | 6 | 148 | 254.7 |
| 6 | 6 | 8 | 7 | 7 | 6 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 6 | 7 | 7 | 9 | 9 | 7 | 6 | 149 | 256.3 |
| 6 | 6 | 8 | 7 | 7 | 6 | 7 | 7 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 6 | 7 | 7 | 9 | 9 | 7 | 6 | 150 | 257.9 |
| 6 | 6 | 8 | 7 | 7 | 6 | 7 | 7 | 7 | 6 | 6 | 6 | 7 | 7 | 7 | 6 | 7 | 7 | 9 | 9 | 7 | 6 | 151 | 259.5 |
| 6 | 6 | 8 | 7 | 7 | 6 | 7 | 7 | 7 | 6 | 6 | 7 | 7 | 7 | 7 | 6 | 7 | 7 | 9 | 9 | 7 | 6 | 152 | 261.1 |
| 6 | 6 | 8 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 6 | 7 | 7 | 9 | 9 | 7 | 6 | 153 | 262.7 |
| 6 | 6 | 8 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 7 | 9 | 9 | 7 | 6 | 154 | 264.3 |
| 7 | 6 | 8 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 7 | 9 | 9 | 7 | 6 | 155 | 265.9 |
| 7 | 6 | 8 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 7 | 9 | 9 | 7 | 7 | 156 | 267.5 |
| 7 | 6 | 9 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 7 | 9 | 9 | 7 | 7 | 157 | 269.1 |
| 7 | 6 | 9 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 7 | 10 | 9 | 7 | 7 | 158 | 270.7 |
| 7 | 6 | 9 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 7 | 10 | 10 | 7 | 7 | 159 | 272.3 |
| 7 | 6 | 9 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 8 | 10 | 10 | 7 | 7 | 160 | 274.0 |
| 7 | 6 | 9 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 8 | 10 | 10 | 8 | 7 | 161 | 275.7 |
| 7 | 6 | 9 | 8 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 8 | 10 | 10 | 8 | 7 | 162 | 277.4 |
| 7 | 6 | 9 | 8 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 8 | 8 | 10 | 10 | 8 | 7 | 163 | 279.1 |
| 7 | 6 | 9 | 8 | 8 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 8 | 8 | 10 | 10 | 8 | 7 | 164 | 280.8 |
| 7 | 6 | 9 | 8 | 8 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 6 | 8 | 8 | 10 | 10 | 8 | 7 | 165 | 282.5 |
| 7 | 6 | 9 | 8 | 8 | 6 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 6 | 8 | 8 | 10 | 10 | 8 | 7 | 166 | 284.2 |
| 7 | 6 | 9 | 8 | 8 | 6 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 6 | 8 | 8 | 10 | 10 | 8 | 7 | 167 | 285.9 |
| 7 | 6 | 9 | 8 | 8 | 6 | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 6 | 8 | 8 | 10 | 10 | 8 | 7 | 168 | 287.6 |
| 7 | 6 | 9 | 8 | 8 | 6 | 8 | 8 | 7 | 7 | 7 | 7 | 8 | 8 | 8 | 6 | 8 | 8 | 10 | 10 | 8 | 7 | 169 | 289.3 |
| 7 | 6 | 9 | 8 | 8 | 6 | 8 | 8 | 8 | 7 | 7 | 7 | 8 | 8 | 8 | 6 | 8 | 8 | 10 | 10 | 8 | 7 | 170 | 291.0 |
| 7 | 6 | 9 | 8 | 8 | 6 | 8 | 8 | 8 | 7 | 7 | 8 | 8 | 8 | 8 | 6 | 8 | 8 | 10 | 10 | 8 | 7 | 171 | 292.7 |
| 7 | 6 | 9 | 8 | 8 | 6 | 8 | 8 | 8 | 8 | 7 | 8 | 8 | 8 | 8 | 6 | 8 | 8 | 10 | 10 | 8 | 7 | 172 | 294.4 |
| 7 | 6 | 9 | 8 | 8 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 8 | 8 | 10 | 10 | 8 | 7 | 173 | 296.1 |
| 8 | 6 | 9 | 8 | 8 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 8 | 8 | 10 | 10 | 8 | 7 | 174 | 297.8 |
| 8 | 6 | 9 | 8 | 8 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 8 | 8 | 10 | 10 | 8 | 8 | 175 | 299.5 |
| 8 | 6 | 10 | 8 | 8 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 8 | 8 | 10 | 10 | 8 | 8 | 176 | 301.1 |