# Fish Passage Plan (FPP) Change Form

Change Form # & Title:	24MCN003 – New Spill Patterns

Date Submitted: 		22-Mar-2024

Project: 			McNary

Requester Name, Agency: 	Chris Peery, Corps NWW

Final Action:

FPP Section:

Chapter 5 (MCN), Section 2.2.5 and new spill pattern tables MCN-8 and MCN-8-ALT.

Justification for Change:

See MFR 24MCN02, emailed to FPOM on 3/22/24.

This FPP Change Form adds the modified spill gate/hoist operation in section 2.2.5 and new spill patterns in Tables MCN-8 and MCN-8-ALT.

The original (pre-2021) patterns in Table MCN-7 will be re-added to the FPP to have a reference for spill patterns under normal operating conditions, per Conder’s request.

Proposed Changes: See following pages.

COMMENTS:

RECORD OF FINAL ACTION:

2.2.5. Interim Modified Spillway Operation

The overloaded condition of McNary Dam spillway cranes and hoists limit their use until they can be replaced. As a result, Cranes 6 and 7 and seven of the 20 hoists can only be used twice per year to move a double-leaf (full) gate, while 13 hoists cannot be used to move a double-leaf gate. Lifting the top leaf of the spill gates will not overload cranes and hoists.

Starting in spring 2024, a total of 13 spill gates and hoists will be operated in the upstream slot in split-leaf configuration. These gates may be adjusted hourly as needed to adjust spill according to patterns in Table MCN-8. The remaining 7 spillbays (1, 2, 3, 5, 8, 15, and 18) will remain closed in the downstream slot in the double-leaf configuration and only opened if needed to pass high flows using the first of two overloaded movements allowed each year. After the high flow event, each gate will be closed using the second overloaded movement allowed that year.

If lower flows are forecasted and meet all hydrologic criteria below, gates 1 and 2 will remain in the downstream slot and opened to 4 stops (~7 kcfs spill) each and spill will be distributed according to patterns in Table MCN-8-ALT:

- Official April water supply forecast for The Dalles April-August runoff below 90 MAF, and

- STP forecast for McNary inflow below 350 kcfs through the spring, and

- Internal weekly Corps system flood risk management (FRM) analyses indicates high probability of McNary inflows below 350 kcfs through the spring.

If the April WSF for The Dalles is greater than 90 MAF, or either the STP or internal Corps FRM analyses indicate flows peaking above 350 kcfs, gates 1 and 2 will remain closed in the downstream slot. Once the risk of inflows exceeding 350 kcfs has passed, and if spill gates 1 and 2 have not yet been opened, the gates will be opened to 4 stops each. Additional downstream gates can be used with a set (e.g., 4 stop) opening after the peak flow period has passed, as coordinated with FPOM.  If gates 1 and 2 are needed to pass higher flows, they will be opened to a level that is expected to be sustained through spring and early summer spill based on the STP and ESP forecasts. Additional gates in the downstream slots will be used to pass higher flows as needed.

If gates 1 and 2 are opened, they will be closed using the second of two allowed overloaded movements at the end of early summer spill on July 31 or once spill is forecast to be below 70 kcfs for the remainder of the spill season.

Table MCN-8. McNary Dam INTERIM Spill Patterns with TSWs in Bays 19-20 and 13 Bays in Split-Leaf in Upstream Slot. a

| Table MCN-8. Interim Patterns w/ 13 Gates in Split Leaf in Upstream Slot (# Gate Stops per Spillbay) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total Stops | Spill |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 b | 20 b | 21 | 22 | (#) | (kcfs) |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TSW | TSW |  |  | 0 | 20.0 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 4 |  | TSW | TSW |  |  | 4 | 25.0 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  | TSW | TSW |  |  | 5 | 26.0 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  | TSW | TSW | 4 |  | 9 | 31.0 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  | TSW | TSW | 5 |  | 10 | 32.0 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  | TSW | TSW | 5 | 4 | 14 | 37.0 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  | TSW | TSW | 5 | 5 | 15 | 38.0 |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 4 |  |  | 5 |  | TSW | TSW | 5 | 5 | 19 | 43.0 |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 20 | 44.0 |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  |  | 6 |  | TSW | TSW | 5 | 5 | 21 | 45.0 |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  |  | 7 |  | TSW | TSW | 5 | 5 | 22 | 46.0 |
|  |  |  |  |  |  |  |  |  |  |  | 4 |  | 5 |  |  | 7 |  | TSW | TSW | 5 | 5 | 26 | 51.0 |
|  |  |  |  |  |  |  |  |  |  |  | 5 |  | 5 |  |  | 7 |  | TSW | TSW | 5 | 5 | 27 | 52.0 |
|  |  |  |  |  |  |  |  |  |  |  | 5 |  | 6 |  |  | 7 |  | TSW | TSW | 5 | 5 | 28 | 53.0 |
|  |  |  |  |  |  |  |  |  |  |  | 5 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 29 | 54.0 |
|  |  |  |  |  |  |  |  |  | 4 |  | 5 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 33 | 59.0 |
|  |  |  |  |  |  |  |  |  | 5 |  | 5 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 34 | 60.0 |
|  |  |  |  |  |  |  |  |  | 5 |  | 6 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 35 | 61.0 |
|  |  |  |  |  |  |  |  |  | 5 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 36 | 62.0 |
|  |  |  | 4 |  |  |  |  |  | 5 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 40 | 67.0 |
|  |  |  | 5 |  |  |  |  |  | 5 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 41 | 68.0 |
|  |  |  | 5 |  |  |  |  |  | 6 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 42 | 69.0 |
|  |  |  | 5 |  |  |  |  |  | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 43 | 70.0 |
|  |  |  | 6 |  |  |  |  |  | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 44 | 71.0 |
|  |  |  | 7 |  |  |  |  |  | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 45 | 72.0 |
|  |  |  | 7 |  | 4 |  |  |  | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 49 | 77.0 |
|  |  |  | 7 |  | 5 |  |  |  | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 50 | 78.0 |
|  |  |  | 8 |  | 5 |  |  |  | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 51 | 79.0 |
|  |  |  | 9 |  | 5 |  |  |  | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 52 | 79.9 |
|  |  |  | 10 |  | 5 |  |  |  | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 53 | 80.8 |
|  |  |  | 10 |  | 6 |  |  |  | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 54 | 81.8 |
|  |  |  | 10 |  | 7 |  |  |  | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 55 | 82.8 |
|  |  |  | 10 |  | 8 |  |  |  | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 56 | 83.8 |
|  |  |  | 10 |  | 9 |  |  |  | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 57 | 84.7 |
|  |  |  | 10 |  | 10 |  |  |  | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 58 | 85.6 |
|  |  |  | 10 |  | 10 |  |  | 4 | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 62 | 90.6 |
|  |  |  | 10 |  | 10 |  |  | 5 | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 63 | 91.6 |
|  |  |  | 10 |  | 10 |  |  | 6 | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 64 | 92.6 |
|  |  |  | 10 |  | 10 |  |  | 7 | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 65 | 93.6 |
|  |  |  | 10 |  | 10 | 4 |  | 7 | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 69 | 98.6 |
|  |  |  | 10 |  | 10 | 5 |  | 7 | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 70 | 99.6 |
|  |  |  | 10 |  | 10 | 6 |  | 7 | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 71 | 100.6 |
|  |  |  | 10 |  | 10 | 7 |  | 7 | 7 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 72 | 101.6 |
|  |  |  | 10 |  | 10 | 7 |  | 7 | 7 |  | 7 |  | 7 |  | 4 | 7 |  | TSW | TSW | 5 | 5 | 76 | 106.6 |
|  |  |  | 10 |  | 10 | 7 |  | 7 | 7 |  | 7 |  | 7 |  | 5 | 7 |  | TSW | TSW | 5 | 5 | 77 | 107.6 |
|  |  |  | 10 |  | 10 | 7 |  | 7 | 7 |  | 7 |  | 7 |  | 6 | 7 |  | TSW | TSW | 5 | 5 | 78 | 108.6 |
|  |  |  | 10 |  | 10 | 7 |  | 7 | 7 |  | 7 |  | 7 |  | 7 | 7 |  | TSW | TSW | 5 | 5 | 79 | 109.6 |
|  |  |  | 10 |  | 10 | 7 |  | 7 | 7 |  | 7 | 4 | 7 |  | 7 | 7 |  | TSW | TSW | 5 | 5 | 83 | 114.6 |
|  |  |  | 10 |  | 10 | 7 |  | 7 | 7 |  | 7 | 5 | 7 |  | 7 | 7 |  | TSW | TSW | 5 | 5 | 84 | 115.6 |
|  |  |  | 10 |  | 10 | 7 |  | 7 | 7 |  | 7 | 6 | 7 |  | 7 | 7 |  | TSW | TSW | 5 | 5 | 85 | 116.6 |
|  |  |  | 10 |  | 10 | 7 |  | 7 | 7 |  | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 5 | 5 | 86 | 117.6 |
|  |  |  | 10 |  | 10 | 7 |  | 7 | 7 | 4 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 5 | 5 | 90 | 122.6 |
|  |  |  | 10 |  | 10 | 7 |  | 7 | 7 | 5 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 5 | 5 | 91 | 123.6 |
|  |  |  | 10 |  | 10 | 7 |  | 7 | 7 | 6 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 5 | 5 | 92 | 124.6 |
|  |  |  | 10 |  | 10 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 5 | 5 | 93 | 125.6 |
|  |  |  | 10 |  | 10 | 8 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 5 | 5 | 94 | 126.6 |
|  |  |  | 10 |  | 10 | 9 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 5 | 5 | 95 | 127.5 |
|  |  |  | 10 |  | 10 | 10 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 5 | 5 | 96 | 128.4 |
|  |  |  | 10 |  | 10 | 10 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 6 | 5 | 97 | 129.4 |
|  |  |  | 10 |  | 10 | 10 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 7 | 5 | 98 | 130.4 |
|  |  |  | 10 |  | 10 | 10 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 7 | 6 | 99 | 131.4 |
|  |  |  | 10 |  | 10 | 10 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 7 | 7 | 100 | 132.4 |
|  |  |  | 11 |  | 10 | 10 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 7 | 7 | 101 | 133.3 |
|  |  |  | 11 |  | 11 | 10 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 7 | 7 | 102 | 134.2 |
|  |  |  | 11 |  | 11 | 11 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 7 | 7 | 103 | 135.1 |
|  |  |  | 11 |  | 11 | 11 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 8 |  | TSW | TSW | 7 | 7 | 104 | 136.1 |
|  |  |  | 11 |  | 11 | 11 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 8 | 8 |  | TSW | TSW | 7 | 7 | 105 | 137.1 |
|  |  |  | 11 |  | 11 | 11 |  | 8 | 7 | 7 | 7 | 7 | 7 |  | 8 | 8 |  | TSW | TSW | 7 | 7 | 106 | 138.1 |
|  |  |  | 11 |  | 11 | 11 |  | 8 | 8 | 7 | 7 | 7 | 8 |  | 8 | 8 |  | TSW | TSW | 7 | 7 | 108 | 140.1 |
|  |  |  | 11 |  | 11 | 11 |  | 8 | 8 | 7 | 7 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 7 | 7 | 109 | 141.1 |
|  |  |  | 11 |  | 11 | 11 |  | 8 | 8 | 8 | 7 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 7 | 7 | 110 | 142.1 |
|  |  |  | 11 |  | 11 | 11 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 7 | 7 | 111 | 143.1 |
|  |  |  | 11 |  | 11 | 11 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 8 | 7 | 112 | 144.1 |
|  |  |  | 11 |  | 11 | 11 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 8 | 8 | 113 | 145.1 |
|  |  |  | 12 |  | 11 | 11 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 8 | 8 | 114 | 146.0 |
|  |  |  | 12 |  | 12 | 11 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 8 | 8 | 115 | 146.9 |
|  |  |  | 12 |  | 12 | 12 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 8 | 8 | 116 | 147.8 |
|  |  |  | 12 |  | 12 | 12 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 9 |  | TSW | TSW | 8 | 8 | 117 | 148.7 |
|  |  |  | 12 |  | 12 | 12 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 9 | 9 |  | TSW | TSW | 8 | 8 | 118 | 149.6 |
|  |  |  | 12 |  | 12 | 12 |  | 9 | 8 | 8 | 8 | 8 | 8 |  | 9 | 9 |  | TSW | TSW | 8 | 8 | 119 | 150.5 |
|  |  |  | 12 |  | 12 | 12 |  | 9 | 9 | 8 | 8 | 8 | 9 |  | 9 | 9 |  | TSW | TSW | 8 | 8 | 121 | 152.3 |
|  |  |  | 12 |  | 12 | 12 |  | 9 | 9 | 8 | 8 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 8 | 8 | 122 | 153.2 |
|  |  |  | 12 |  | 12 | 12 |  | 9 | 9 | 9 | 8 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 8 | 8 | 123 | 154.1 |
|  |  |  | 12 |  | 12 | 12 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 8 | 8 | 124 | 155.0 |
|  |  |  | 12 |  | 12 | 12 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 9 | 8 | 125 | 155.9 |
|  |  |  | 12 |  | 12 | 12 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 9 | 9 | 126 | 156.8 |
|  |  |  | 13 |  | 12 | 12 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 9 | 9 | 127 | 157.5 |
|  |  |  | 13 |  | 13 | 12 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 9 | 9 | 128 | 158.2 |
|  |  |  | 13 |  | 13 | 13 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 9 | 9 | 129 | 158.9 |
|  |  |  | 13 |  | 13 | 13 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 10 |  | TSW | TSW | 9 | 9 | 130 | 159.8 |
|  |  |  | 13 |  | 13 | 13 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 10 | 10 |  | TSW | TSW | 9 | 9 | 131 | 160.7 |
|  |  |  | 13 |  | 13 | 13 |  | 10 | 9 | 9 | 9 | 9 | 9 |  | 10 | 10 |  | TSW | TSW | 9 | 9 | 132 | 161.6 |
|  |  |  | 13 |  | 13 | 13 |  | 10 | 10 | 9 | 9 | 9 | 10 |  | 10 | 10 |  | TSW | TSW | 9 | 9 | 134 | 163.4 |
|  |  |  | 13 |  | 13 | 13 |  | 10 | 10 | 9 | 9 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 9 | 9 | 135 | 164.3 |
|  |  |  | 13 |  | 13 | 13 |  | 10 | 10 | 10 | 9 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 9 | 9 | 136 | 165.2 |
|  |  |  | 13 |  | 13 | 13 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 9 | 9 | 137 | 166.1 |
|  |  |  | 13 |  | 13 | 13 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 10 | 9 | 138 | 167.0 |
|  |  |  | 13 |  | 13 | 13 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 10 | 10 | 139 | 167.9 |
|  |  |  | 14 |  | 13 | 13 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 10 | 10 | 140 | 168.7 |
|  |  |  | 14 |  | 14 | 13 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 10 | 10 | 141 | 169.5 |
|  |  |  | 14 |  | 14 | 14 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 10 | 10 | 142 | 170.3 |
|  |  |  | 14 |  | 14 | 14 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 11 |  | TSW | TSW | 10 | 10 | 143 | 171.2 |
|  |  |  | 14 |  | 14 | 14 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 11 | 11 |  | TSW | TSW | 10 | 10 | 144 | 172.1 |
|  |  |  | 14 |  | 14 | 14 |  | 11 | 10 | 10 | 10 | 10 | 10 |  | 11 | 11 |  | TSW | TSW | 10 | 10 | 145 | 173.0 |
|  |  |  | 14 |  | 14 | 14 |  | 11 | 11 | 10 | 10 | 10 | 11 |  | 11 | 11 |  | TSW | TSW | 10 | 10 | 147 | 174.8 |
|  |  |  | 14 |  | 14 | 14 |  | 11 | 11 | 10 | 10 | 11 | 11 |  | 11 | 11 |  | TSW | TSW | 10 | 10 | 148 | 175.7 |
|  |  |  | 14 |  | 14 | 14 |  | 11 | 11 | 11 | 10 | 11 | 11 |  | 11 | 11 |  | TSW | TSW | 10 | 10 | 149 | 176.6 |
|  |  |  | 14 |  | 14 | 14 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 |  | TSW | TSW | 10 | 10 | 150 | 177.5 |
|  |  |  | 14 |  | 14 | 14 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 |  | TSW | TSW | 11 | 10 | 151 | 178.4 |
|  |  |  | 14 |  | 14 | 14 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 |  | TSW | TSW | 11 | 11 | 152 | 179.3 |
|  |  |  | 15 |  | 14 | 14 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 |  | TSW | TSW | 11 | 11 | 153 | 180.1 |
|  |  |  | 15 |  | 15 | 14 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 |  | TSW | TSW | 11 | 11 | 154 | 180.9 |
|  |  |  | 15 |  | 15 | 15 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 |  | TSW | TSW | 11 | 11 | 155 | 181.7 |
|  |  |  | 15 |  | 15 | 15 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 12 |  | TSW | TSW | 11 | 11 | 156 | 182.6 |
|  |  |  | 15 |  | 15 | 15 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 12 | 12 |  | TSW | TSW | 11 | 11 | 157 | 183.5 |
|  |  |  | 15 |  | 15 | 15 |  | 12 | 11 | 11 | 11 | 11 | 11 |  | 12 | 12 |  | TSW | TSW | 11 | 11 | 158 | 184.4 |
|  |  |  | 15 |  | 15 | 15 |  | 12 | 12 | 11 | 11 | 11 | 12 |  | 12 | 12 |  | TSW | TSW | 11 | 11 | 160 | 186.2 |
|  |  |  | 15 |  | 15 | 15 |  | 12 | 12 | 11 | 11 | 12 | 12 |  | 12 | 12 |  | TSW | TSW | 11 | 11 | 161 | 187.1 |
|  |  |  | 15 |  | 15 | 15 |  | 12 | 12 | 12 | 11 | 12 | 12 |  | 12 | 12 |  | TSW | TSW | 11 | 11 | 162 | 188.0 |
|  |  |  | 15 |  | 15 | 15 |  | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 |  | TSW | TSW | 11 | 11 | 163 | 188.9 |
|  |  |  | 15 |  | 15 | 15 |  | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 |  | TSW | TSW | 12 | 11 | 164 | 189.8 |
|  |  |  | 15 |  | 15 | 15 |  | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 |  | TSW | TSW | 12 | 12 | 165 | 190.7 |
|  |  |  | 15 |  | 15 | 15 |  | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 13 |  | TSW | TSW | 12 | 12 | 166 | 191.4 |
|  |  |  | 15 |  | 15 | 15 |  | 12 | 12 | 12 | 12 | 12 | 12 |  | 13 | 13 |  | TSW | TSW | 12 | 12 | 167 | 192.1 |
|  |  |  | 15 |  | 15 | 15 |  | 13 | 12 | 12 | 12 | 12 | 12 |  | 13 | 13 |  | TSW | TSW | 12 | 12 | 168 | 192.8 |
|  |  |  | 15 |  | 15 | 15 |  | 13 | 13 | 12 | 12 | 12 | 13 |  | 13 | 13 |  | TSW | TSW | 12 | 12 | 170 | 194.2 |
|  |  |  | 15 |  | 15 | 15 |  | 13 | 13 | 12 | 12 | 13 | 13 |  | 13 | 13 |  | TSW | TSW | 12 | 12 | 171 | 194.9 |
|  |  |  | 15 |  | 15 | 15 |  | 13 | 13 | 13 | 12 | 13 | 13 |  | 13 | 13 |  | TSW | TSW | 12 | 12 | 172 | 195.6 |
|  |  |  | 15 |  | 15 | 15 |  | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 |  | TSW | TSW | 12 | 12 | 173 | 196.3 |
|  |  |  | 15 |  | 15 | 15 |  | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 |  | TSW | TSW | 13 | 12 | 174 | 197.0 |
|  |  |  | 15 |  | 15 | 15 |  | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 |  | TSW | TSW | 13 | 13 | 175 | 197.7 |
|  |  |  | 15 |  | 15 | 15 |  | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 14 |  | TSW | TSW | 13 | 13 | 176 | 198.5 |
|  |  |  | 15 |  | 15 | 15 |  | 13 | 13 | 13 | 13 | 13 | 13 |  | 14 | 14 |  | TSW | TSW | 13 | 13 | 177 | 199.3 |
|  |  |  | 15 |  | 15 | 15 |  | 14 | 13 | 13 | 13 | 13 | 13 |  | 14 | 14 |  | TSW | TSW | 13 | 13 | 178 | 200.1 |
|  |  |  | 15 |  | 15 | 15 |  | 14 | 14 | 13 | 13 | 13 | 14 |  | 14 | 14 |  | TSW | TSW | 13 | 13 | 180 | 201.7 |
|  |  |  | 15 |  | 15 | 15 |  | 14 | 14 | 13 | 13 | 14 | 14 |  | 14 | 14 |  | TSW | TSW | 13 | 13 | 181 | 202.5 |
|  |  |  | 15 |  | 15 | 15 |  | 14 | 14 | 14 | 13 | 14 | 14 |  | 14 | 14 |  | TSW | TSW | 13 | 13 | 182 | 203.3 |
|  |  |  | 15 |  | 15 | 15 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 |  | TSW | TSW | 13 | 13 | 183 | 204.1 |
|  |  |  | 15 |  | 15 | 15 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 |  | TSW | TSW | 14 | 13 | 184 | 204.9 |
|  |  |  | 15 |  | 15 | 15 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 |  | TSW | TSW | 14 | 14 | 185 | 205.7 |
|  |  |  | 15 |  | 15 | 15 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 15 |  | TSW | TSW | 14 | 14 | 186 | 206.5 |
|  |  |  | 15 |  | 15 | 15 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 15 | 15 |  | TSW | TSW | 14 | 14 | 187 | 207.3 |
|  |  |  | 15 |  | 15 | 15 |  | 15 | 14 | 14 | 14 | 14 | 14 |  | 15 | 15 |  | TSW | TSW | 14 | 14 | 188 | 208.1 |
|  |  |  | 15 |  | 15 | 15 |  | 15 | 15 | 14 | 14 | 14 | 15 |  | 15 | 15 |  | TSW | TSW | 14 | 14 | 190 | 209.7 |
|  |  |  | 15 |  | 15 | 15 |  | 15 | 15 | 14 | 14 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 14 | 14 | 191 | 210.5 |
|  |  |  | 15 |  | 15 | 15 |  | 15 | 15 | 15 | 14 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 14 | 14 | 192 | 211.3 |
|  |  |  | 15 |  | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 14 | 14 | 193 | 212.1 |
|  |  |  | 15 |  | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 15 | 14 | 194 | 212.9 |
|  |  |  | 15 |  | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 15 | 15 | 195 | 213.7 |
|  |  |  | 19 |  | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 15 | 15 | 199 | 217.4 |
|  |  |  | 19 |  | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 15 | 19 | 203 | 221.1 |
|  |  |  | 19 |  | 19 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 15 | 19 | 207 | 224.8 |
|  |  |  | 19 |  | 19 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 19 | 19 | 211 | 228.5 |
|  |  |  | 19 |  | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 19 | 19 | 215 | 232.2 |
|  |  |  | 19 |  | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 19 |  | TSW | TSW | 19 | 19 | 219 | 235.9 |
|  |  |  | 19 |  | 19 | 19 |  | 19 | 15 | 15 | 15 | 15 | 15 |  | 15 | 19 |  | TSW | TSW | 19 | 19 | 223 | 239.6 |
|  |  |  | 19 |  | 19 | 19 |  | 19 | 15 | 15 | 15 | 15 | 15 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 227 | 243.3 |
|  |  |  | 19 |  | 19 | 19 |  | 19 | 19 | 15 | 15 | 15 | 15 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 231 | 247.0 |
|  |  |  | 19 |  | 19 | 19 |  | 19 | 19 | 15 | 15 | 15 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 235 | 250.7 |
|  |  |  | 19 |  | 19 | 19 |  | 19 | 19 | 19 | 15 | 15 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 239 | 254.4 |
|  |  |  | 19 |  | 19 | 19 |  | 19 | 19 | 19 | 15 | 19 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 243 | 258.1 |
|  |  |  | 19 |  | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 247 | 261.8 |
|  | 20 |  | 19 |  | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 19 | 19 | 235 | 264.3 |
|  | 20 |  | 19 |  | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 19 |  | TSW | TSW | 19 | 19 | 239 | 268.0 |
|  | 20 |  | 19 |  | 19 | 19 |  | 19 | 15 | 15 | 15 | 15 | 15 |  | 15 | 19 |  | TSW | TSW | 19 | 19 | 243 | 271.7 |
|  | 20 |  | 19 |  | 19 | 19 |  | 19 | 15 | 15 | 15 | 15 | 15 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 247 | 275.4 |
|  | 20 |  | 19 |  | 19 | 19 |  | 19 | 19 | 15 | 15 | 15 | 15 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 251 | 279.1 |
|  | 20 |  | 19 |  | 19 | 19 |  | 19 | 19 | 15 | 15 | 15 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 255 | 282.8 |
|  | 20 |  | 19 |  | 19 | 19 |  | 19 | 19 | 19 | 15 | 15 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 259 | 286.5 |
|  | 20 |  | 19 |  | 19 | 19 |  | 19 | 19 | 19 | 15 | 19 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 263 | 290.2 |
|  | 20 |  | 19 |  | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 267 | 293.9 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 19 | 19 | 255 | 296.4 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 19 |  | TSW | TSW | 19 | 19 | 259 | 300.1 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 15 | 15 | 15 | 15 | 15 |  | 15 | 19 |  | TSW | TSW | 19 | 19 | 263 | 303.8 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 15 | 15 | 15 | 15 | 15 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 267 | 307.5 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 15 | 15 | 15 | 15 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 271 | 311.2 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 15 | 15 | 15 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 275 | 314.9 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 15 | 15 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 279 | 318.6 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 15 | 19 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 283 | 322.3 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 287 | 326.0 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 20 | TSW | TSW | 19 | 19 | 275 | 328.5 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 19 | 20 | TSW | TSW | 19 | 19 | 279 | 332.2 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 15 | 15 | 15 | 15 | 15 |  | 15 | 19 | 20 | TSW | TSW | 19 | 19 | 283 | 335.9 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 15 | 15 | 15 | 15 | 15 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 287 | 339.6 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 15 | 15 | 15 | 15 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 291 | 343.3 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 15 | 15 | 15 | 19 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 295 | 347.0 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 15 | 15 | 19 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 299 | 350.7 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 15 | 19 | 19 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 303 | 354.4 |
|  | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 307 | 358.1 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 20 | TSW | TSW | 19 | 19 | 295 | 360.6 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 19 | 20 | TSW | TSW | 19 | 19 | 299 | 364.3 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 15 | 15 | 15 | 15 | 15 |  | 15 | 19 | 20 | TSW | TSW | 19 | 19 | 303 | 368.0 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 15 | 15 | 15 | 15 | 15 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 307 | 371.7 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 15 | 15 | 15 | 15 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 311 | 375.4 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 15 | 15 | 15 | 19 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 315 | 379.1 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 15 | 15 | 19 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 319 | 382.8 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 15 | 19 | 19 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 323 | 386.5 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 327 | 390.2 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 15 | 15 | 20 | TSW | TSW | 19 | 19 | 315 | 392.7 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 15 | 19 | 20 | TSW | TSW | 19 | 19 | 319 | 396.4 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 15 | 15 | 15 | 15 | 15 | 20 | 15 | 19 | 20 | TSW | TSW | 19 | 19 | 323 | 400.1 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 15 | 15 | 15 | 15 | 15 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 327 | 403.8 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 15 | 15 | 15 | 15 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 331 | 407.5 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 15 | 15 | 15 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 335 | 411.2 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 15 | 15 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 339 | 414.9 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 15 | 19 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 343 | 418.6 |
| 20 | 20 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 347 | 422.3 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 15 | 15 | 20 | TSW | TSW | 19 | 19 | 335 | 424.8 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 15 | 19 | 20 | TSW | TSW | 19 | 19 | 339 | 428.5 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 |  | 19 | 15 | 15 | 15 | 15 | 15 | 20 | 15 | 19 | 20 | TSW | TSW | 19 | 19 | 343 | 432.2 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 |  | 19 | 15 | 15 | 15 | 15 | 15 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 347 | 435.9 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 |  | 19 | 19 | 15 | 15 | 15 | 15 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 351 | 439.6 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 |  | 19 | 19 | 15 | 15 | 15 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 355 | 443.3 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 15 | 15 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 359 | 447.0 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 15 | 19 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 363 | 450.7 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 367 | 454.4 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 15 | 15 | 20 | TSW | TSW | 19 | 19 | 355 | 456.9 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 15 | 19 | 20 | TSW | TSW | 19 | 19 | 359 | 460.6 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 15 | 15 | 15 | 15 | 15 | 20 | 15 | 19 | 20 | TSW | TSW | 19 | 19 | 363 | 464.3 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 15 | 15 | 15 | 15 | 15 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 367 | 468.0 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 15 | 15 | 15 | 15 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 371 | 471.7 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 15 | 15 | 15 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 375 | 475.4 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 19 | 15 | 15 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 379 | 479.1 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 19 | 15 | 19 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 383 | 482.8 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 387 | 486.5 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 20 | 21 | TSW | 19 | 19 | 408 | 496.5 |
| 20 | 20 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 20 | 21 | 21 | 19 | 19 | 429 | 506.5 |
| 20 | Free | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 20 | 21 | 21 | 19 | 19 | 409 | 536.6 |
| 20 | Free | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | Free | 21 | 21 | 19 | 19 | 389 | 566.7 |
| 20 | Free | 20 | 19 | Free | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | Free | 21 | 21 | 19 | 19 | 369 | 596.8 |
| 20 | Free | 20 | 19 | Free | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | Free | 19 | 19 | Free | 21 | 21 | 19 | 19 | 349 | 626.9 |
| 20 | Free | 20 | 19 | Free | 19 | 19 | Free | 19 | 19 | 19 | 19 | 19 | 19 | Free | 19 | 19 | Free | 21 | 21 | 19 | 19 | 329 | 657.0 |
| Free | Free | 20 | 19 | Free | 19 | 19 | Free | 19 | 19 | 19 | 19 | 19 | 19 | Free | 19 | 19 | Free | 21 | 21 | 19 | 19 | 309 | 687.1 |
| Free | Free | Free | 19 | Free | 19 | 19 | Free | 19 | 19 | 19 | 19 | 19 | 19 | Free | 19 | 19 | Free | 21 | 21 | 19 | 19 | 289 | 717.2 |

- A total of 13 spill gates and hoists will be operated in the upstream slot in split-leaf configuration and adjusted hourly as needed to adjust spill. The remaining 7 spillbays (1, 2, 3, 5, 8, 15, and 18) will remain closed in the downstream slot in double-leaf and only opened if needed to pass high flows using the first of two overloaded movements allowed each year. After the high flow event, open double-leaf gates will be closed using the second of two allowed overloaded movements.

- Bays 19-20 with TSWs spill approx 19.2 kcfs (9.6 kcfs/bay) at forebay 339'. The upper TSW gates will be raised 3-5 ft above the water surface to ensure free flow over the TSW crests.

Table MCN-8-ALT. McNary Dam INTERIM Spill Patterns with TSWs in Bays 19-20 and 13 Bays in Split-Leaf (upstream slot) and Bays 1&2 Available. a, b

| Table MCN-8-ALT. Interim Patterns w/ 13 Gates in Split Leaf in Upstream Slot and Bays 1&2 Available (# Gate Stops per Spillbay) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total Stops | Spill |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 c | 20 c | 21 | 22 | (#) | (kcfs) |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TSW | TSW |  |  | 0 | 19.4 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 4 |  | TSW | TSW |  |  | 4 | 24.4 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  | TSW | TSW |  |  | 5 | 25.4 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  | TSW | TSW | 4 |  | 9 | 30.4 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  | TSW | TSW | 5 |  | 10 | 31.4 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  | TSW | TSW | 5 | 4 | 14 | 36.4 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  | TSW | TSW | 5 | 5 | 15 | 37.4 |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 4 |  |  | 5 |  | TSW | TSW | 5 | 5 | 19 | 42.4 |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 20 | 43.4 |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  |  | 6 |  | TSW | TSW | 5 | 5 | 21 | 44.4 |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 5 |  |  | 7 |  | TSW | TSW | 5 | 5 | 22 | 45.4 |
|  |  |  |  |  |  |  |  |  |  |  | 4 |  | 5 |  |  | 7 |  | TSW | TSW | 5 | 5 | 26 | 50.4 |
|  |  |  |  |  |  |  |  |  |  |  | 5 |  | 5 |  |  | 7 |  | TSW | TSW | 5 | 5 | 27 | 51.4 |
|  |  |  |  |  |  |  |  |  |  |  | 5 |  | 6 |  |  | 7 |  | TSW | TSW | 5 | 5 | 28 | 52.4 |
|  |  |  |  |  |  |  |  |  |  |  | 5 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 29 | 53.4 |
|  |  |  |  |  |  |  |  |  | 4 |  | 5 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 33 | 58.4 |
|  |  |  |  |  |  |  |  |  | 5 |  | 5 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 34 | 59.4 |
|  |  |  |  |  |  |  |  |  | 5 |  | 6 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 35 | 60.4 |
|  |  |  |  |  |  |  |  |  | 5 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 36 | 61.4 |
|  |  |  | 4 |  |  |  |  |  | 5 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 40 | 66.4 |
|  |  |  | 5 |  |  |  |  |  | 5 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 41 | 67.4 |
|  |  |  | 6 |  |  |  |  |  | 5 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 42 | 68.4 |
|  |  |  | 7 |  |  |  |  |  | 5 |  | 7 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 43 | 69.4 |
| 4 | 4 |  | 5 |  |  |  |  |  | 4 |  | 4 |  | 4 |  |  | 4 |  | TSW | TSW | 5 | 5 | 39 | 71.4 |
| 4 | 4 |  | 5 |  |  |  |  |  | 4 |  | 4 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 41 | 73.4 |
| 4 | 4 |  | 5 |  |  |  |  |  | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 43 | 75.4 |
| 4 | 4 |  | 5 |  |  |  |  |  | 5 |  | 5 |  | 5 |  |  | 7 |  | TSW | TSW | 5 | 5 | 45 | 77.4 |
| 4 | 4 |  | 5 |  |  |  |  |  | 5 |  | 5 |  | 7 |  |  | 7 |  | TSW | TSW | 5 | 5 | 47 | 79.4 |
| 4 | 4 |  | 5 |  | 4 |  |  |  | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 47 | 80.4 |
| 4 | 4 |  | 6 |  | 5 |  |  |  | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 49 | 82.4 |
| 4 | 4 |  | 7 |  | 5 |  |  |  | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 50 | 83.4 |
| 4 | 4 |  | 7 |  | 6 |  |  |  | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 51 | 84.4 |
| 4 | 4 |  | 8 |  | 6 |  |  |  | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 52 | 85.4 |
| 4 | 4 |  | 8 |  | 7 |  |  |  | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 53 | 86.4 |
| 4 | 4 |  | 9 |  | 7 |  |  |  | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 54 | 87.3 |
| 4 | 4 |  | 9 |  | 8 |  |  |  | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 55 | 88.3 |
| 4 | 4 |  | 10 |  | 8 |  |  |  | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 56 | 89.2 |
| 4 | 4 |  | 10 |  | 8 |  |  | 4 | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 60 | 94.2 |
| 4 | 4 |  | 10 |  | 8 |  |  | 5 | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 61 | 95.2 |
| 4 | 4 |  | 10 |  | 9 |  |  | 5 | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 62 | 96.1 |
| 4 | 4 |  | 10 |  | 10 |  |  | 5 | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 63 | 97.0 |
| 4 | 4 |  | 10 |  | 7 | 4 |  | 5 | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 64 | 99.2 |
| 4 | 4 |  | 10 |  | 9 | 5 |  | 5 | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 67 | 102.1 |
| 4 | 4 |  | 10 |  | 9 | 6 |  | 5 | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 68 | 103.1 |
| 4 | 4 |  | 10 |  | 10 | 6 |  | 5 | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 69 | 104.0 |
| 4 | 4 |  | 10 |  | 10 | 7 |  | 5 | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 70 | 105.0 |
| 4 | 4 |  | 10 |  | 10 | 9 |  | 5 | 5 |  | 5 |  | 5 |  |  | 5 |  | TSW | TSW | 5 | 5 | 72 | 106.9 |
| 4 | 4 |  | 10 |  | 10 | 7 |  | 5 | 5 |  | 5 |  | 5 |  | 4 | 5 |  | TSW | TSW | 5 | 5 | 74 | 110.0 |
| 4 | 4 |  | 10 |  | 10 | 7 |  | 5 | 5 |  | 5 |  | 5 |  | 5 | 5 |  | TSW | TSW | 5 | 5 | 75 | 111.0 |
| 4 | 4 |  | 10 |  | 10 | 7 |  | 5 | 5 |  | 5 |  | 5 |  | 5 | 6 |  | TSW | TSW | 5 | 5 | 76 | 112.0 |
| 4 | 4 |  | 10 |  | 10 | 7 |  | 5 | 5 |  | 5 |  | 5 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 77 | 113.0 |
| 4 | 4 |  | 10 |  | 10 | 8 |  | 5 | 5 |  | 5 |  | 5 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 78 | 114.0 |
| 4 | 4 |  | 10 |  | 10 | 7 |  | 5 | 5 |  | 5 | 4 | 5 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 81 | 118.0 |
| 4 | 4 |  | 10 |  | 10 | 7 |  | 5 | 5 |  | 5 | 5 | 5 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 82 | 119.0 |
| 4 | 4 |  | 10 |  | 10 | 7 |  | 6 | 5 |  | 5 | 5 | 5 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 83 | 120.0 |
| 4 | 4 |  | 10 |  | 10 | 7 |  | 6 | 6 |  | 5 | 5 | 5 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 84 | 121.0 |
| 4 | 4 |  | 10 |  | 10 | 7 |  | 5 | 5 | 4 | 5 | 5 | 5 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 86 | 124.0 |
| 4 | 4 |  | 10 |  | 10 | 7 |  | 5 | 5 | 5 | 5 | 5 | 5 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 87 | 125.0 |
| 4 | 4 |  | 10 |  | 10 | 7 |  | 6 | 5 | 5 | 5 | 5 | 5 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 88 | 126.0 |
| 4 | 4 |  | 10 |  | 10 | 7 |  | 6 | 6 | 5 | 5 | 5 | 5 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 89 | 127.0 |
| 4 | 4 |  | 10 |  | 10 | 8 |  | 6 | 6 | 5 | 5 | 5 | 5 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 90 | 128.0 |
| 4 | 4 |  | 10 |  | 10 | 8 |  | 6 | 6 | 5 | 5 | 5 | 6 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 91 | 129.0 |
| 4 | 4 |  | 10 |  | 10 | 8 |  | 6 | 6 | 5 | 5 | 6 | 6 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 92 | 130.0 |
| 4 | 4 |  | 10 |  | 10 | 8 |  | 6 | 6 | 5 | 6 | 6 | 6 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 93 | 131.0 |
| 4 | 4 |  | 10 |  | 10 | 8 |  | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 |  | TSW | TSW | 5 | 5 | 94 | 132.0 |
| 4 | 4 |  | 10 |  | 10 | 8 |  | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 |  | TSW | TSW | 6 | 5 | 95 | 133.0 |
| 4 | 4 |  | 10 |  | 10 | 8 |  | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 |  | TSW | TSW | 6 | 6 | 96 | 134.0 |
| 4 | 4 |  | 10 |  | 10 | 9 |  | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 |  | TSW | TSW | 6 | 6 | 97 | 134.9 |
| 4 | 4 |  | 10 |  | 10 | 9 |  | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 7 |  | TSW | TSW | 6 | 6 | 98 | 135.9 |
| 4 | 4 |  | 10 |  | 10 | 9 |  | 6 | 6 | 6 | 6 | 6 | 6 |  | 7 | 7 |  | TSW | TSW | 6 | 6 | 99 | 136.9 |
| 4 | 4 |  | 11 |  | 10 | 9 |  | 7 | 6 | 6 | 6 | 6 | 6 |  | 7 | 7 |  | TSW | TSW | 6 | 6 | 101 | 138.8 |
| 4 | 4 |  | 11 |  | 10 | 9 |  | 7 | 7 | 6 | 6 | 6 | 6 |  | 7 | 7 |  | TSW | TSW | 6 | 6 | 102 | 139.8 |
| 4 | 4 |  | 11 |  | 10 | 9 |  | 7 | 7 | 6 | 6 | 6 | 7 |  | 7 | 7 |  | TSW | TSW | 6 | 6 | 103 | 140.8 |
| 4 | 4 |  | 11 |  | 10 | 9 |  | 7 | 7 | 6 | 6 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 6 | 6 | 104 | 141.8 |
| 4 | 4 |  | 11 |  | 10 | 9 |  | 7 | 7 | 7 | 6 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 6 | 6 | 105 | 142.8 |
| 4 | 4 |  | 11 |  | 10 | 9 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 6 | 6 | 106 | 143.8 |
| 4 | 4 |  | 11 |  | 10 | 9 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 7 | 6 | 107 | 144.8 |
| 4 | 4 |  | 11 |  | 10 | 9 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 7 | 7 | 108 | 145.8 |
| 4 | 4 |  | 11 |  | 10 | 10 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 7 | 7 | 109 | 146.7 |
| 4 | 4 |  | 11 |  | 11 | 10 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 |  | TSW | TSW | 7 | 7 | 110 | 147.6 |
| 4 | 4 |  | 11 |  | 11 | 10 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 8 |  | TSW | TSW | 7 | 7 | 111 | 148.6 |
| 4 | 4 |  | 11 |  | 11 | 10 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | 8 | 8 |  | TSW | TSW | 7 | 7 | 112 | 149.6 |
| 4 | 4 |  | 11 |  | 11 | 10 |  | 8 | 7 | 7 | 7 | 7 | 7 |  | 8 | 8 |  | TSW | TSW | 7 | 7 | 113 | 150.6 |
| 4 | 4 |  | 11 |  | 11 | 10 |  | 8 | 8 | 7 | 7 | 7 | 7 |  | 8 | 8 |  | TSW | TSW | 7 | 7 | 114 | 151.6 |
| 4 | 4 |  | 11 |  | 11 | 10 |  | 8 | 8 | 7 | 7 | 7 | 8 |  | 8 | 8 |  | TSW | TSW | 7 | 7 | 115 | 152.6 |
| 4 | 4 |  | 11 |  | 11 | 10 |  | 8 | 8 | 7 | 7 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 7 | 7 | 116 | 153.6 |
| 4 | 4 |  | 11 |  | 11 | 10 |  | 8 | 8 | 8 | 7 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 7 | 7 | 117 | 154.6 |
| 4 | 4 |  | 11 |  | 11 | 10 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 7 | 7 | 118 | 155.6 |
| 4 | 4 |  | 11 |  | 11 | 10 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 8 | 7 | 119 | 156.6 |
| 4 | 4 |  | 11 |  | 11 | 10 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 8 | 8 | 120 | 157.6 |
| 4 | 4 |  | 12 |  | 11 | 10 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 8 | 8 | 121 | 158.5 |
| 4 | 4 |  | 12 |  | 12 | 10 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 8 | 8 | 122 | 159.4 |
| 4 | 4 |  | 12 |  | 12 | 11 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 |  | TSW | TSW | 8 | 8 | 123 | 160.3 |
| 4 | 4 |  | 12 |  | 12 | 11 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 9 |  | TSW | TSW | 8 | 8 | 124 | 161.2 |
| 4 | 4 |  | 12 |  | 12 | 11 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 9 | 9 |  | TSW | TSW | 8 | 8 | 125 | 162.1 |
| 4 | 4 |  | 12 |  | 12 | 11 |  | 9 | 8 | 8 | 8 | 8 | 8 |  | 9 | 9 |  | TSW | TSW | 8 | 8 | 126 | 163.0 |
| 4 | 4 |  | 12 |  | 12 | 11 |  | 9 | 9 | 8 | 8 | 8 | 9 |  | 9 | 9 |  | TSW | TSW | 8 | 8 | 128 | 164.8 |
| 4 | 4 |  | 12 |  | 12 | 11 |  | 9 | 9 | 8 | 8 | 8 | 9 |  | 9 | 9 |  | TSW | TSW | 8 | 8 | 128 | 164.8 |
| 4 | 4 |  | 12 |  | 12 | 11 |  | 9 | 9 | 8 | 8 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 8 | 8 | 129 | 165.7 |
| 4 | 4 |  | 12 |  | 12 | 11 |  | 9 | 9 | 9 | 8 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 8 | 8 | 130 | 166.6 |
| 4 | 4 |  | 12 |  | 12 | 11 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 8 | 8 | 131 | 167.5 |
| 4 | 4 |  | 12 |  | 12 | 11 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 9 | 8 | 132 | 168.4 |
| 4 | 4 |  | 12 |  | 12 | 11 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 9 | 9 | 133 | 169.3 |
| 4 | 4 |  | 13 |  | 12 | 11 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 9 | 9 | 134 | 170.0 |
| 4 | 4 |  | 13 |  | 13 | 11 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 9 | 9 | 135 | 170.7 |
| 4 | 4 |  | 13 |  | 13 | 12 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 |  | TSW | TSW | 9 | 9 | 136 | 171.6 |
| 4 | 4 |  | 13 |  | 13 | 12 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 10 |  | TSW | TSW | 9 | 9 | 137 | 172.5 |
| 4 | 4 |  | 13 |  | 13 | 12 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 10 | 10 |  | TSW | TSW | 9 | 9 | 138 | 173.4 |
| 4 | 4 |  | 13 |  | 13 | 12 |  | 10 | 9 | 9 | 9 | 9 | 10 |  | 10 | 10 |  | TSW | TSW | 9 | 9 | 140 | 175.2 |
| 4 | 4 |  | 13 |  | 13 | 12 |  | 10 | 10 | 9 | 9 | 9 | 9 |  | 10 | 10 |  | TSW | TSW | 9 | 9 | 140 | 175.2 |
| 4 | 4 |  | 13 |  | 13 | 12 |  | 10 | 10 | 9 | 9 | 9 | 10 |  | 10 | 10 |  | TSW | TSW | 9 | 9 | 141 | 176.1 |
| 4 | 4 |  | 13 |  | 13 | 12 |  | 10 | 10 | 10 | 9 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 9 | 9 | 143 | 177.9 |
| 4 | 4 |  | 13 |  | 13 | 12 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 10 | 9 | 145 | 179.7 |
| 4 | 4 |  | 13 |  | 13 | 12 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 10 | 10 | 146 | 180.6 |
| 4 | 4 |  | 14 |  | 13 | 12 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 10 | 10 | 147 | 181.4 |
| 4 | 4 |  | 14 |  | 13 | 12 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 10 | 10 | 147 | 181.4 |
| 4 | 4 |  | 14 |  | 14 | 12 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 10 | 10 | 148 | 182.2 |
| 4 | 4 |  | 14 |  | 14 | 13 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | TSW | TSW | 10 | 10 | 149 | 182.9 |
| 4 | 4 |  | 14 |  | 14 | 13 |  | 11 | 10 | 10 | 10 | 10 | 10 |  | 10 | 11 |  | TSW | TSW | 10 | 10 | 151 | 184.7 |
| 4 | 4 |  | 14 |  | 14 | 13 |  | 11 | 10 | 10 | 10 | 10 | 10 |  | 11 | 11 |  | TSW | TSW | 10 | 10 | 152 | 185.6 |
| 4 | 4 |  | 14 |  | 14 | 13 |  | 11 | 11 | 10 | 10 | 10 | 11 |  | 11 | 11 |  | TSW | TSW | 10 | 10 | 154 | 187.4 |
| 4 | 4 |  | 14 |  | 14 | 13 |  | 11 | 11 | 10 | 10 | 10 | 11 |  | 11 | 11 |  | TSW | TSW | 10 | 10 | 154 | 187.4 |
| 4 | 4 |  | 14 |  | 14 | 13 |  | 11 | 11 | 10 | 10 | 10 | 11 |  | 11 | 11 |  | TSW | TSW | 10 | 10 | 154 | 187.4 |
| 4 | 4 |  | 14 |  | 14 | 13 |  | 11 | 11 | 11 | 10 | 11 | 11 |  | 11 | 11 |  | TSW | TSW | 10 | 10 | 156 | 189.2 |
| 4 | 4 |  | 14 |  | 14 | 13 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 |  | TSW | TSW | 10 | 10 | 157 | 190.1 |
| 4 | 4 |  | 14 |  | 14 | 13 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 |  | TSW | TSW | 11 | 10 | 158 | 191.0 |
| 4 | 4 |  | 14 |  | 14 | 13 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 |  | TSW | TSW | 11 | 11 | 159 | 191.9 |
| 4 | 4 |  | 15 |  | 14 | 13 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 |  | TSW | TSW | 11 | 11 | 160 | 192.7 |
| 4 | 4 |  | 15 |  | 15 | 13 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 |  | TSW | TSW | 11 | 11 | 161 | 193.5 |
| 4 | 4 |  | 15 |  | 15 | 14 |  | 11 | 11 | 11 | 11 | 11 | 12 |  | 11 | 11 |  | TSW | TSW | 11 | 11 | 163 | 195.2 |
| 4 | 4 |  | 15 |  | 15 | 14 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 12 |  | TSW | TSW | 11 | 11 | 163 | 195.2 |
| 4 | 4 |  | 15 |  | 15 | 14 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 12 | 12 |  | TSW | TSW | 11 | 11 | 164 | 196.1 |
| 4 | 4 |  | 15 |  | 15 | 14 |  | 12 | 11 | 11 | 11 | 11 | 11 |  | 12 | 12 |  | TSW | TSW | 11 | 11 | 165 | 197.0 |
| 4 | 4 |  | 15 |  | 15 | 14 |  | 12 | 12 | 11 | 11 | 11 | 12 |  | 12 | 12 |  | TSW | TSW | 11 | 11 | 167 | 198.8 |
| 4 | 4 |  | 15 |  | 15 | 14 |  | 12 | 12 | 11 | 11 | 12 | 12 |  | 12 | 12 |  | TSW | TSW | 11 | 11 | 168 | 199.7 |
| 4 | 4 |  | 15 |  | 15 | 14 |  | 12 | 12 | 12 | 11 | 12 | 12 |  | 12 | 12 |  | TSW | TSW | 11 | 11 | 169 | 200.6 |
| 4 | 4 |  | 15 |  | 15 | 14 |  | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 |  | TSW | TSW | 11 | 11 | 170 | 201.5 |
| 4 | 4 |  | 15 |  | 15 | 14 |  | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 |  | TSW | TSW | 12 | 11 | 171 | 202.4 |
| 4 | 4 |  | 15 |  | 15 | 14 |  | 12 | 12 | 12 | 12 | 12 | 13 |  | 12 | 12 |  | TSW | TSW | 12 | 12 | 173 | 204.0 |
| 4 | 4 |  | 16 |  | 15 | 14 |  | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 |  | TSW | TSW | 12 | 12 | 173 | 204.3 |
| 4 | 4 |  | 16 |  | 16 | 14 |  | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 |  | TSW | TSW | 12 | 12 | 174 | 205.3 |
| 4 | 4 |  | 16 |  | 16 | 15 |  | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 |  | TSW | TSW | 12 | 12 | 175 | 206.1 |
| 4 | 4 |  | 16 |  | 16 | 15 |  | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 13 |  | TSW | TSW | 12 | 12 | 176 | 206.8 |
| 4 | 4 |  | 16 |  | 16 | 15 |  | 12 | 12 | 12 | 12 | 12 | 12 |  | 13 | 13 |  | TSW | TSW | 12 | 12 | 177 | 207.5 |
| 4 | 4 |  | 16 |  | 16 | 15 |  | 13 | 12 | 12 | 12 | 12 | 12 |  | 13 | 13 |  | TSW | TSW | 12 | 12 | 178 | 208.2 |
| 4 | 4 |  | 16 |  | 16 | 15 |  | 13 | 13 | 12 | 12 | 12 | 13 |  | 13 | 13 |  | TSW | TSW | 12 | 12 | 180 | 209.6 |
| 4 | 4 |  | 16 |  | 16 | 15 |  | 13 | 13 | 12 | 12 | 13 | 13 |  | 13 | 13 |  | TSW | TSW | 12 | 12 | 181 | 210.3 |
| 4 | 4 |  | 16 |  | 16 | 15 |  | 13 | 13 | 13 | 12 | 13 | 13 |  | 13 | 13 |  | TSW | TSW | 12 | 12 | 182 | 211.0 |
| 4 | 4 |  | 16 |  | 16 | 15 |  | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 |  | TSW | TSW | 12 | 12 | 183 | 211.7 |
| 4 | 4 |  | 16 |  | 16 | 15 |  | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 |  | TSW | TSW | 13 | 12 | 184 | 212.4 |
| 4 | 4 |  | 16 |  | 16 | 15 |  | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 |  | TSW | TSW | 13 | 13 | 185 | 213.1 |
| 4 | 4 |  | 17 |  | 16 | 15 |  | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 |  | TSW | TSW | 13 | 13 | 186 | 214.0 |
| 4 | 4 |  | 17 |  | 17 | 15 |  | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 |  | TSW | TSW | 13 | 13 | 187 | 214.9 |
| 4 | 4 |  | 17 |  | 17 | 16 |  | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 |  | TSW | TSW | 13 | 13 | 188 | 215.9 |
| 4 | 4 |  | 17 |  | 17 | 16 |  | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 14 |  | TSW | TSW | 13 | 13 | 189 | 216.7 |
| 4 | 4 |  | 17 |  | 17 | 16 |  | 13 | 13 | 13 | 13 | 13 | 13 |  | 14 | 14 |  | TSW | TSW | 13 | 13 | 190 | 217.5 |
| 4 | 4 |  | 17 |  | 17 | 16 |  | 14 | 13 | 13 | 13 | 13 | 13 |  | 14 | 14 |  | TSW | TSW | 13 | 13 | 191 | 218.3 |
| 4 | 4 |  | 17 |  | 17 | 16 |  | 14 | 14 | 13 | 13 | 13 | 14 |  | 14 | 14 |  | TSW | TSW | 13 | 13 | 193 | 219.9 |
| 4 | 4 |  | 17 |  | 17 | 16 |  | 14 | 14 | 14 | 13 | 14 | 14 |  | 14 | 14 |  | TSW | TSW | 13 | 13 | 195 | 221.5 |
| 4 | 4 |  | 17 |  | 17 | 16 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 |  | TSW | TSW | 13 | 13 | 196 | 222.3 |
| 4 | 4 |  | 17 |  | 17 | 16 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 |  | TSW | TSW | 14 | 13 | 197 | 223.1 |
| 4 | 4 |  | 17 |  | 17 | 16 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 |  | TSW | TSW | 14 | 14 | 198 | 223.9 |
| 4 | 4 |  | 18 |  | 17 | 16 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 |  | TSW | TSW | 14 | 14 | 199 | 224.8 |
| 4 | 4 |  | 18 |  | 18 | 16 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 |  | TSW | TSW | 14 | 14 | 200 | 225.7 |
| 4 | 4 |  | 18 |  | 18 | 17 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 |  | TSW | TSW | 14 | 14 | 201 | 226.6 |
| 4 | 4 |  | 18 |  | 18 | 17 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 15 |  | TSW | TSW | 14 | 14 | 202 | 227.4 |
| 4 | 4 |  | 18 |  | 18 | 17 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 15 | 15 |  | TSW | TSW | 14 | 14 | 203 | 228.2 |
| 4 | 4 |  | 18 |  | 18 | 17 |  | 15 | 14 | 14 | 14 | 14 | 14 |  | 15 | 15 |  | TSW | TSW | 14 | 14 | 204 | 229.0 |
| 4 | 4 |  | 18 |  | 18 | 17 |  | 15 | 15 | 14 | 14 | 14 | 15 |  | 15 | 15 |  | TSW | TSW | 14 | 14 | 206 | 230.6 |
| 4 | 4 |  | 18 |  | 18 | 17 |  | 15 | 15 | 15 | 14 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 14 | 14 | 208 | 232.2 |
| 4 | 4 |  | 18 |  | 18 | 17 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 15 | 14 | 210 | 233.8 |
| 4 | 4 |  | 18 |  | 18 | 17 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 15 | 15 | 211 | 234.6 |
| 4 | 4 |  | 19 |  | 18 | 17 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 15 | 15 | 212 | 235.5 |
| 4 | 4 |  | 19 |  | 19 | 17 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 15 | 15 | 213 | 236.4 |
| 4 | 4 |  | 19 |  | 19 | 18 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 15 | 15 | 214 | 237.3 |
| 4 | 4 |  | 19 |  | 19 | 18 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 16 |  | TSW | TSW | 15 | 15 | 215 | 238.3 |
| 4 | 4 |  | 19 |  | 19 | 18 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 16 | 16 |  | TSW | TSW | 15 | 15 | 216 | 239.3 |
| 4 | 4 |  | 19 |  | 19 | 18 |  | 16 | 15 | 15 | 15 | 15 | 15 |  | 16 | 16 |  | TSW | TSW | 15 | 15 | 217 | 240.3 |
| 4 | 4 |  | 19 |  | 19 | 18 |  | 16 | 16 | 15 | 15 | 15 | 16 |  | 16 | 16 |  | TSW | TSW | 15 | 15 | 219 | 242.3 |
| 4 | 4 |  | 19 |  | 19 | 18 |  | 16 | 16 | 16 | 15 | 16 | 16 |  | 16 | 16 |  | TSW | TSW | 15 | 15 | 221 | 244.3 |
| 4 | 4 |  | 19 |  | 19 | 18 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 |  | TSW | TSW | 15 | 15 | 222 | 245.3 |
| 4 | 4 |  | 19 |  | 19 | 18 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 |  | TSW | TSW | 16 | 15 | 223 | 246.3 |
| 4 | 4 |  | 19 |  | 19 | 18 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 |  | TSW | TSW | 16 | 16 | 224 | 247.3 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 |  | TSW | TSW | 16 | 16 | 225 | 248.2 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 17 |  | TSW | TSW | 16 | 16 | 226 | 249.1 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 17 | 17 |  | TSW | TSW | 16 | 16 | 227 | 250.0 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 17 | 16 | 16 | 16 | 16 | 16 |  | 17 | 17 |  | TSW | TSW | 16 | 16 | 228 | 250.9 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 17 | 17 | 16 | 16 | 16 | 17 |  | 17 | 17 |  | TSW | TSW | 16 | 16 | 230 | 252.7 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 17 | 17 | 17 | 16 | 17 | 17 |  | 17 | 17 |  | TSW | TSW | 16 | 16 | 232 | 254.5 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 |  | TSW | TSW | 16 | 16 | 233 | 255.4 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 |  | TSW | TSW | 16 | 17 | 234 | 256.3 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 |  | TSW | TSW | 17 | 17 | 235 | 257.2 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 18 |  | TSW | TSW | 17 | 17 | 236 | 258.1 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 18 | 18 |  | TSW | TSW | 17 | 17 | 237 | 259.0 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 18 | 17 | 17 | 17 | 17 | 17 |  | 18 | 18 |  | TSW | TSW | 17 | 17 | 238 | 259.9 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 18 | 18 | 17 | 17 | 17 | 18 |  | 18 | 18 |  | TSW | TSW | 17 | 17 | 240 | 261.7 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 18 | 18 | 18 | 17 | 18 | 18 |  | 18 | 18 |  | TSW | TSW | 17 | 17 | 242 | 263.5 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 |  | TSW | TSW | 17 | 17 | 243 | 264.4 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 |  | TSW | TSW | 17 | 18 | 244 | 265.3 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 |  | TSW | TSW | 18 | 18 | 245 | 266.2 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 19 |  | TSW | TSW | 18 | 18 | 246 | 267.1 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 |  | 19 | 19 |  | TSW | TSW | 18 | 18 | 247 | 268.0 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 19 | 18 | 18 | 18 | 18 | 18 |  | 19 | 19 |  | TSW | TSW | 18 | 18 | 248 | 268.9 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 19 | 19 | 18 | 18 | 18 | 19 |  | 19 | 19 |  | TSW | TSW | 18 | 18 | 250 | 270.7 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 19 | 19 | 19 | 18 | 19 | 19 |  | 19 | 19 |  | TSW | TSW | 18 | 18 | 252 | 272.5 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 |  | TSW | TSW | 18 | 18 | 253 | 273.4 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 |  | TSW | TSW | 18 | 19 | 254 | 274.3 |
| 4 | 4 |  | 19 |  | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 255 | 275.2 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 |  | TSW | TSW | 19 | 19 | 243 | 277.7 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 16 |  | TSW | TSW | 19 | 19 | 244 | 278.7 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 16 | 16 |  | TSW | TSW | 19 | 19 | 245 | 279.7 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 16 | 15 | 15 | 15 | 15 | 15 |  | 16 | 16 |  | TSW | TSW | 19 | 19 | 246 | 280.7 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 16 | 16 | 15 | 15 | 15 | 16 |  | 16 | 16 |  | TSW | TSW | 19 | 19 | 248 | 282.7 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 16 | 16 | 16 | 15 | 16 | 16 |  | 16 | 16 |  | TSW | TSW | 19 | 19 | 250 | 284.7 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 |  | TSW | TSW | 19 | 19 | 251 | 285.7 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 17 |  | TSW | TSW | 19 | 19 | 252 | 286.6 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 17 | 17 |  | TSW | TSW | 19 | 19 | 253 | 287.5 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 17 | 16 | 16 | 16 | 16 | 16 |  | 17 | 17 |  | TSW | TSW | 19 | 19 | 254 | 288.4 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 17 | 17 | 16 | 16 | 16 | 17 |  | 17 | 17 |  | TSW | TSW | 19 | 19 | 256 | 290.2 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 17 | 17 | 17 | 16 | 17 | 17 |  | 17 | 17 |  | TSW | TSW | 19 | 19 | 258 | 292.0 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 |  | TSW | TSW | 19 | 19 | 259 | 292.9 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 18 | 18 |  | TSW | TSW | 19 | 19 | 261 | 294.7 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 18 | 17 | 17 | 17 | 17 | 17 |  | 18 | 18 |  | TSW | TSW | 19 | 19 | 262 | 295.6 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 18 | 18 | 16 | 17 | 17 | 18 |  | 18 | 18 |  | TSW | TSW | 19 | 19 | 263 | 296.5 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 18 | 18 | 18 | 17 | 18 | 18 |  | 18 | 18 |  | TSW | TSW | 19 | 19 | 266 | 299.2 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 |  | TSW | TSW | 19 | 19 | 267 | 300.1 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 19 |  | TSW | TSW | 19 | 19 | 268 | 301.0 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 269 | 301.9 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 19 | 18 | 18 | 18 | 18 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 271 | 303.7 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 18 | 18 | 19 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 273 | 305.5 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 |  | TSW | TSW | 19 | 19 | 275 | 307.3 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 20 | TSW | TSW | 19 | 19 | 263 | 309.8 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 265 | 311.8 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 16 | 15 | 15 | 15 | 15 | 16 |  | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 267 | 313.8 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 16 | 16 | 15 | 15 | 16 | 16 |  | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 269 | 315.8 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 271 | 317.8 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 273 | 319.6 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 17 | 16 | 16 | 16 | 16 | 17 |  | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 275 | 321.4 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 17 | 17 | 16 | 16 | 17 | 17 |  | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 277 | 323.2 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 279 | 325.0 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 281 | 326.8 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 18 | 17 | 17 | 17 | 17 | 18 |  | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 283 | 328.6 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 18 | 18 | 16 | 17 | 18 | 18 |  | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 284 | 329.5 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 287 | 332.2 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 289 | 334.0 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 19 | 18 | 18 | 18 | 18 | 19 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 291 | 335.8 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 18 | 18 | 19 | 19 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 293 | 337.6 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 295 | 339.4 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 15 | 15 | 20 | TSW | TSW | 19 | 19 | 283 | 341.9 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 285 | 343.9 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 16 | 15 | 15 | 15 | 15 | 16 | 20 | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 287 | 345.9 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 16 | 16 | 15 | 15 | 16 | 16 | 20 | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 289 | 347.9 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 291 | 349.9 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 293 | 351.7 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 17 | 16 | 16 | 16 | 16 | 17 | 20 | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 295 | 353.5 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 17 | 17 | 16 | 16 | 17 | 17 | 20 | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 297 | 355.3 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 299 | 357.1 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 301 | 358.9 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 18 | 17 | 17 | 17 | 17 | 18 | 20 | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 303 | 360.7 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 18 | 18 | 17 | 17 | 18 | 18 | 20 | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 305 | 362.5 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 307 | 364.3 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 309 | 366.1 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 19 | 18 | 18 | 18 | 18 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 311 | 367.9 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 18 | 18 | 19 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 313 | 369.7 |
| 4 | 4 |  | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 315 | 371.5 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 15 | 15 | 20 | TSW | TSW | 19 | 19 | 303 | 374.0 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 305 | 376.0 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 16 | 15 | 15 | 15 | 15 | 16 | 20 | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 307 | 378.0 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 16 | 16 | 15 | 15 | 16 | 16 | 20 | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 309 | 380.0 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 311 | 382.0 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 313 | 383.8 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 17 | 16 | 16 | 16 | 16 | 17 | 20 | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 315 | 385.6 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 17 | 17 | 16 | 16 | 17 | 17 | 20 | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 317 | 387.4 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 319 | 389.2 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 321 | 391.0 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 18 | 17 | 17 | 17 | 17 | 18 | 20 | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 323 | 392.8 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 18 | 18 | 17 | 17 | 18 | 18 | 20 | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 325 | 394.6 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 327 | 396.4 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 329 | 398.2 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 19 | 18 | 18 | 18 | 18 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 331 | 400.0 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 19 | 19 | 18 | 18 | 19 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 333 | 401.8 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 335 | 403.6 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 15 | 15 | 20 | TSW | TSW | 19 | 19 | 323 | 406.1 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 325 | 408.1 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 16 | 15 | 15 | 15 | 15 | 16 | 20 | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 327 | 410.1 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 16 | 16 | 15 | 15 | 16 | 16 | 20 | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 329 | 412.1 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 16 | 16 | 20 | TSW | TSW | 19 | 19 | 331 | 414.1 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 333 | 415.9 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 17 | 16 | 16 | 16 | 16 | 17 | 20 | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 335 | 417.7 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 17 | 17 | 16 | 16 | 17 | 17 | 20 | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 337 | 419.5 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 17 | 17 | 20 | TSW | TSW | 19 | 19 | 339 | 421.3 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 341 | 423.1 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 18 | 17 | 17 | 17 | 17 | 18 | 20 | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 343 | 424.9 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 18 | 18 | 17 | 17 | 18 | 18 | 20 | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 345 | 426.7 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 18 | 18 | 20 | TSW | TSW | 19 | 19 | 347 | 428.5 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 349 | 430.3 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 18 | 18 | 18 | 18 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 351 | 432.1 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 18 | 18 | 19 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 353 | 433.9 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 20 | TSW | TSW | 19 | 19 | 355 | 435.7 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 20 | 21 | TSW | 19 | 19 | 376 | 446.0 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 20 | 21 | 21 | 19 | 19 | 397 | 456.3 |
| 4 | 4 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | Free | 21 | 21 | 19 | 19 | 377 | 486.4 |
| 4 | 4 | 20 | 19 | Free | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | Free | 21 | 21 | 19 | 19 | 357 | 516.5 |
| 4 | 4 | 20 | 19 | Free | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | Free | 19 | 19 | Free | 21 | 21 | 19 | 19 | 337 | 546.6 |
| 4 | 4 | 20 | 19 | Free | 19 | 19 | Free | 19 | 19 | 19 | 19 | 19 | 19 | Free | 19 | 19 | Free | 21 | 21 | 19 | 19 | 317 | 576.7 |
| 4 | 4 | Free | 19 | Free | 19 | 19 | Free | 19 | 19 | 19 | 19 | 19 | 19 | Free | 19 | 19 | Free | 21 | 21 | 19 | 19 | 297 | 606.8 |

- These alternate patterns in Table MCN-8-ALT will be used if low flows are forecasted and meet all hydrologic criteria defined in section 2.2.5. Spill gates 1 and 2 will be opened once to 4 stops (~7 kcfs per bay) then remain open at 4 stops through early summer spill on July 31, or when flows drop below 70 kcfs. Opening and closing gates 1&2 will use both overloaded movements allowed each year.

- A total of 13 spill gates and hoists will be operated in the upstream slot in split-leaf and adjusted hourly as needed to adjust spill. The remaining 5 spillbays (3, 5, 8, 15, and 18) will remain closed in the downstream slot in double-leaf and only opened if needed to pass high flows using the first of two overloaded movements allowed each year. After the high flow event, open double-leaf gates will be closed using the second of two allowed overloaded movements.

- Bays 19-20 with TSWs spill approx 19.2 kcfs (9.6 kcfs/bay) at forebay 339'. The upper TSW gates will be raised 3-5 ft above the water surface to ensure free flow over the TSW crests.