## NWW
Project | Location | Work Item | Comment - Red highlighted items currently affect meeting FPP criteria. | NWW | NOAA | USFWS | CRITFC | WDFW | IDFG | ODFW | Average | Notes
All | Bypass system | Critical spare parts | Lack of sufficient spare parts required juvenile passage to be in emergency bypass March 2021 | 4 | 5 | 4 | 4 | 5 | 5 |  | 4.5 | Change the average to incorporate 7 instead of 6 ranks.
All Projects | Spillway | Sediment Recruitment Prevention | Reduce entrainment of debris to spillwy stilling basins
All Projects | Bypass Systems | Vertical Barrier Screen (VBS) and Submerged Travelling Screen (STS) Rehab | Replace vertical bar/screen material. Rehab
Ice Harbor | Spillway | Rehab spillway gates | High trunnion friction and lowered structural integrity from age create risk of failure. Gates are experiencing significant corrosion to tension tie bolts, gusset plates, and skin plates. | 5 | 4 | 4 | 4 | 4 |  |  | 4.2 | If safety is a concern, WDFW is willing to rank it a 5.
Ice Harbor | Fishways | AWS pump rehab | Aging pumps have high risk of failure | 3 | 5 | 4 | 4 | 4 | 4 |  | 4
Ice Harbor | Fishways | Entrance hoists and controls replacement | Hoists have failed causing fishway to be temporarily closed and out of criteria | 3 | 4 | 5 | 3 | 3 | 4 |  | 3.6667
Ice Harbor | Spillway | Spillway crane and stop logs replacement | The crane has frequent failures, and operates at an extremely slow pace, which affects Ice Harbor's ability to lower stoplogs and conduct maintenance, emergency, or fish passage operations. Scheduled for appropriations FY25. | 4 | 4 | 3 | 3 | 4 |  |  | 3.6
Ice Harbor | Forebay | Ladder exit debris booms | Current log booms are old and are prone to failure with east winds | 3 | 3 | 3 | 3 | 3 | 2 |  | 2.8333
Ice Harbor | Juvenile fish channel | Expansion of air burst cleaning system under inclined screen | Material purchase needed to keep screens clear of debris | 3 | 3 | 3 | 3 | 3 | 2 |  | 2.8333
Ice Harbor | Fish count station | Air motors for window brushes | $2500 per motor | 3 | 3 | 3 | 2 | 3 | 1 |  | 2.5
Ice Harbor | Juvenile fish channel | Spare actuator for water regulating weirs |  | 2 | 3 | 2 | 2 | 2 | 1 |  | 2
Ice Harbor | JFF | Juvenile Fish Outfall Pipe Access Walkway | Can only access outfall pipe by boat for maintenenace and repairs
Little Goose | North shore | Replace north shore jetty | Lost during high flows, protects north shore fishway entrance from shore eddy | 3 | 5 | 3 | 4 | 3 | 5 |  | 3.8333
Little Goose | Fishway | Replace fishway control system | Fishway entrances operate in manual mode only, requiring regular inspections and manual adjustments to maintain fishway criteria | 4 | 4 | 5 | 3 | 3 | 4 |  | 3.8333
Little Goose | Fishway | Re-design fish count station | Turbulence interferes with accurate fish counting | 4 | 3 | 4 | 3 | 4 | 2 |  | 3.3333
Little Goose | Fishway | Replace diffuser grating and support beams | Diffuser grates are corroded and failing. Broken grates risk injury and mortality to adult salmon passing dams | 3 | 3 | 3 | 3 | 3 | 2 |  | 2.8333
Little Goose | Collection channel | Repair/replace corroded outer steel orifice pipe with stainless steal | Orifices have failed mid-season causing them to be closed until winter maintenance period | 3 | 3 | 3 | 3 | 3 | 2 |  | 2.8333
Little Goose | Collection channel | Repair orifice valve cylinders |  | 3 | 3 | 2 | 3 | 3 | 3 |  | 2.8333
Little Goose | Fishway | Repair or replace fishway cooling pump and spare | Original fishway cooling pump and spare have failed and need to be repaired. Third pump has been purchased. | 5 | 5 | 5 | 5 | 5 |  |  | 5
LMN, LGS, LWG | Powerhouse deck | T1/T2 spare transformer | New - In process. Would be aplicable to mutiple dams. T1C showing elevated gas levels that may lead to derating of T1 units. | 5 | 4 | 4 | 3 | 4 | 0 |  | 3.3333 | FPOM has concerns about how this is related to fish passage. | IDFG - Not fish-facility maintenance = 0; connection to fish passage is adult passage under a partial or whole powerhouse outage; however, this should not be put forward as fish focused. This is transmission infrastructure.
Lower Monumental | Forebay | Install shear boom to move debris to spillway | Debris can enter juvenile bypass system, risking injury and mortality to juvenile salmonids | 3 | 5 | 4 | 3 | 3 | 3 |  | 3.5
Lower Monumental | JFF | Primary Dewaterer repairs | Worn brass nuts, missing motor, weir held in place with chain | 3 | 3 | 4 | 3 | 3 | 3 |  | 3.1667
Lower Monumental | Spillway | Update Spillway Gate Bushings Oil System | New - In process | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 |  | 3 w/ caveat. This is important for fish passage, but it is more important for dam safety and should be put forward as such.
Lower Monumental | Spillway | Spillway Gate Hoist System Rehab | Gears show excessive wear. Parts being procured to make temporary repairs but gearboxes will need replacement | 5 | 4 | 5 | 5 | 5 |  |  | 4.8
Lower Monumental | Fishway | Replace diffuser gratings and grate supports | Diffuser grates are corroded and failing. Broken grates risk injury and mortality to adult salmon passing dams
Lower Granite | Fishway | Modify fishway cooling pump outflow | By rerouting some pump flow to fishway exit pool we can improve temperature conditions at top of fishway | 4 | 4 | 4 | 4 | 4 |  |  | 4
Lower Granite | Fishway | Adult shad deterrence | Develop methods to block adult shad from passing project
Lower Granite | Fishway | Rehad/replace fishway AWS pumps | Age and condition of pumps create high risk of failure. | 4 | 4 | 4 | 4 | 4 | 5 |  | 4.1667
Lower Granite | Fishways | Rehad/replace fishway entrances. NSE1 and NSE2 are showing cracks in the concrete | Age and condition of fishway entrances create relatively high risk for failure | 4 | 4 | 4 | 3 | 4 | 4 |  | 3.8333
Lower Granite | Barges | Improve degassing system on 2000 barges | Current pumping system is inadequate to degass river water during periods of high TDG | 4 | 4 | 4 | 3 | 5 | 1 |  | 3.5
Lower Granite | Fishway | Correct Control System Programing malfunction | Control system is not accurate, requiring regular inspections and manual adjustments to maintain fishway criteria | 4 | 3 | 5 | 3 | 3 | 3 |  | 3.5
Lower Granite | Fishway | Install/replace velocity meter in channel | Current system not working, provides inaccurate readings | 3 | 3 | 3 | 3 | 3 | 2 |  | 2.8333
Lower Granite | JFF | Complete Phase 1a modifications and resolve programing issues. | PDW/JBS | 2 | 2 | 3 | 2 | 2 | 1 |  | 2
Lower Granite | Fishway | Permanently close floating orifice gates not used | Reduce leaking and annual maintenenace of stoplogs | 2 | 2 | 3 | 2 | 2 | 1 |  | 2
Lower Granite | Fishway | NSE, SSE, and NPE local depth indication | Current system not working, provides inaccurate readings | 2 | 2 | 2 | 2 | 2 | 1 |  | 1.8333
McNary | Oregon Fishway | Replace AWS fishway pumps | Condition of pumps results in being off line often for repairs. Pump 3 currently OOS. Two pumps have been OOS at times in recent years. | 5 | 5 | 5 | 5 | 5 | 5 |  | 5
McNary | Spillway | Replace spillway cranes, hoists, and gates | Cranes and hoists underrated for lifting requirements and often OOS for repairs because of age and condition (Items 2,3,4 on NWW List) | 5 | 5 | 4 | 5 | 5 | 5 |  | 4.8333
McNary | Spillway | Add hoists to spillbays 2 and 19 | Spillbays 2 and 19 do not contain hoists and can only be operated using two spillway cranes. | 5 | 4 | 4 | 5 | 5 | 5 |  | 4.6667
McNary | Oregon Fishway | Rejuvenate dewatering system; Replace transverse stoplog guides. | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 4 | 4 | 4 | 4 | 3 |  | 3.8333
McNary | Oregon Fishway | Rejuvenate dewatering system; Rehabilitate all transverse stoplogs. | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 4 | 4 | 4 | 4 | 3 |  | 3.8333
McNary | Oregon Fishway | Rejuvenate dewatering system; replace rotovalves, slide gates | Project cannot currently dewater south shore fishway to affect repairs. See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 4 | 4 | 4 | 4 | 3 |  | 3.8333
McNary | Oregon Fishway | Rejuvenate dewatering system; Rehabilitate all floating weirs and guides | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 4 | 4 | 4 | 4 | 3 |  | 3.8333
McNary | Oregon Fishway | Replace diffuser gratings and grate supports | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 5 | 4 | 3 | 4 | 3 |  | 3.8333
McNary | Oregon Fishway | Permanently close floating orifice gates not used | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 3 | 2 | 2 | 3 | 3 | 2 |  | 2.5
McNary | Spillway | Update repair pit | Stress cracks in dogs and other damage require repairs to all gates spillgates similar to work conducted on spillgate 16 in 2023. Work began with FY23 funds. Eventually replace all gates. | 4 | 4 | 3 | 3 | 4 |  |  | 3.6 | This item needs to be edited to reflect just the repair pit.
McNary | JFF Bypass System | Upgrade the Primary Dewatering Structure Flow Controls
All ranking is 1-5, similar to SCT.
1 = lowest 5 = highest priority
indicates "defer to Corps"
Note on F16: Trevor Conder: Increased from a 2
Note on F20: Trevor Conder: Why is this still "Unfunded" at this point in time?
Note on F31: Trevor Conder: Reduced from 5 since TDG eval showed may not be a big issue.
Note on F38: Trevor Conder: Increased from 4
Note on F39: Trevor Conder: Increased from 3

## NWP
Ranked 5-1, with 5 high and 1 low. Yellow highlight indicates deference to Corps ranking.
Project | Work Package Title | Condition / Description of Unsatisfactory Performance | Consequences of the Unsatisfactory Performance (Budget Justification) | NWP | NOAA | USFWS | CRITFC | WDFW | IDFG | ODFW | Average -
Bonneville | Fish Ladder, Bradford Island A Branch Auxiliary water supply conduit (AWS) Joint Repair | The conduit is not watertight and the significant leaks have resulted in a sinkhole and a small geyser that is undermining a sidewalk and potentially the ladder itself. Past repairs have not been able to adequately address the failure. | Failure of this conduit results in a complete stoppage of adult fish passage in the A-branch of the Bradford Island fish ladder. This would violate the Fish Passage Plan/BiOp. | 5 | 5 | 5 | 5 | 5 | 5 |  | 5
Bonneville | Fish Ladder, Bradford Island A Branch Fish valves (FV1-2, 3-7, 3-9) | These valves provide all of the water for the A-branch, both for fish attraction and to the diffusers. These valves are original equipment from the 1930s, and are in need of refurbishment. FV 1-2 is currently only used under special circumstances due to its condition. | Failure of these valves results in a complete stoppage of adult fish passage in the A-branch of the Bradford Island fish ladder. This would violate the Fish Passage Plan/BiOp. | 5 | 4 | 4 | 4 | 4 | 5 |  | 4.3333
Bonneville | Replace & Secure Diffuser Grating B1 | Grating is aged, deteriorating, and is repaired during fishway maintenance every other year. Full replacement will reduce burden on routine O&M for many years | Failure of these gratings could result in fish entrapment and/or mortality. Failure would require a costly dewater of the auxiliary water systems potentially occurring during peak fish passage season causing increased mortality rate of ESA listed species. | 4 | 5 | 4 | 4 | 5 | 4 |  | 4.3333
Bonneville | B2 Replace & Secure Diffuser Grating | Grating has deteriorated to the point that it is unsafe to walk on when the channel is dewatered. | Grating has deteriorated to the point that it is unsafe to walk on when the channel is dewatered. Potential failures impact upstream migration of adult salmonids leading to mortality and non-compliance of BiOp and Fish Passage Plan requirements. Grating failures may require the entire auxiliary water system to be dewatered to effect repairs and salvage fish. These out-of-cycle emergency repairs (historically $600K) put personnel at risk. | 4 | 4 | 4 | 4 | 4 | 4 |  | 4
Bonneville | Replace/Modernize Spillway OPTO Control System. The design is near completion. Need purchase of fiber, new switches and PLCs. This is a multi-year project with P&S and Construction. | Spillway power, unwatering pumps and other critical equipment are controlled by a single system (PLC interfaces). The current system is past its useful life and spare parts can no longer be procurred. Failures will result in loss of remote monitoring and control of one or more bays | Replace/Modernize Spillway OPTO Control System. The design is near completion. Need purchase of fiber, new switches and PLCs. This is a multi-year project with P&S and Construction. | 4 | 3 | 4 | 4 | 4 | 4 |  | 3.8333
Bonneville | Bradford Island Fish Ladder Exit | Bradford Island Fishladder Exit requires expensive O&M dredging. A newly designed and built exit channel would remove the need for maintenance dredging in the future | Repeated bi-annual dredging ($250K every 2 years) is required to keep fish ladder exit area deep enough for adult fish passage. | 3 | 3 | 4 | 4 | 4 | 4 |  | 3.6667
Bonneville | Remove Fish Valve 3-8 which separates the auxiliary water supplies of the A-branch conduit and the collection channel conduit. | Valve is obsolete and inherently carries a risk of failure between the conduits. | Removing the obsolete valve and permanently isolating these two conduits will avoid a failure that would remove Bradford Island Fishladder from service and force the fishway out of compliance with the Fish Passage Plan. | 4 | 3 | 4 | 3 | 4 | 4 |  | 3.6667
Bonneville | B1 Fishway Controls | Update fishway controls system. Current fishway controls are a mix of old systems that do not allow for master control and single point monitoring. Master controls and single point monitoring allows operators and fish biologists to operate Fishway controls in a precise manner, monitor changes instantaneously and gather data to support biological studies and implement historian for trend evaluation. Additionally, systems upgrades extend our capabilities to remote program, apply system updates, increase cyber security and ease maintenance and troubleshooting. | There is a single, very outdated (1989) control center responsible for fishway ops at B1 (above refers to the entire BI fishway) to include diffusers, valves that feed diffusers, and entrance gates. This control center is non reparable and nonreplaceable. Once it dies, every piece of equipment will have to be adjusted manually until the new system can be completed. The work is estimate to take 2-3 months, and would include CI, BI, & PH1 (everything other than PH2). | 4 | 3 | 4 | 3 | 4 | 3 |  | 3.5
Bonneville | Bonneville 1 Fish Ladder Diffuser (P&S $2.1M) (Construction $9.7M) | The diffuser valves are failing and require replacement. Stimulus funds provided plans and specifications for the necessary repairs. | Failure of one diffuser results in out of criteria status with the Fish Passage Plan/BiOP. Failure of more than one cannot be worked around and will limit or preclude fish passage. | 4 | 3 | 3 | 3 | 3 | 4 |  | 3.3333
Bonneville | Purchase and install screen and valve pit bulkheads to facilitate de-watering operations of the Bradford Island and Cascade Island fish passage systems. | Limited number of bulkheads reduces the ability to inspect and repair one of the two systems on scheduled reoccurring cycles. | Failure of one fish passage system resulting in placement of bulkheads will not allow for removal of second fishway system due to lack of bulkheads resulting in violation of BiOp. | 3 | 3 |  | 2 | 2 | 2 |  | 2.4
Bonneville | JMF build out - office space for FFU + Dive | THE FFU trailer is reaching the natural end of life. One option is to build out the JMF with modular offices and move FFU there. This will keep FFU behind secure gates and reduce Corps presence on the penninsula (which may help with hatchery disposal at some point in the future). |  | 3 | 1 |  | 3 | 3 | 1 |  | 2.2
Bonneville | Redesign FV 3-7 & 3-9 Intakes and purchase mechanized trash rake. 2 year project with Construction being completed in an even numbered fiscal year during annual overhaul. This is a 2 year project with P&S $100k and Construction $400k. | Current process requires three employees being exposed to hazardous conditions from working over water. | Redesign FV 3-7 & 3-9 intakes and purchase mechanized trash rake. Current process requires three employees being exposed to hazardous conditions from working over water. Fish valve intakes need to be redesigned to accommodate automated rake. Mechanized rake would reduce labor hours and potential for injury from removing heavy wet debris from the river and allow for removing material the full length of the trash rack. Mechanized rake will reduce the manhours, duration, cycling of automated control equipment, and allow for seven day coverage. Reduction of debris loading of trash racks will aid in compliance with fish passage plan requirements. | 2 | 1 |  | 2 | 2 | 2 |  | 1.8
Bonneville | Spillway Fish Elevators | Fish elevators are non-functional, have not been used in at least 50 years, and are an environmental and safety hazard. Fish elevators need to be decommissioned and removed from the project. The existing areas should be cleaned up and be made available for other uses. | Environmental issues due to potential oil spillage. May have wooden bulkheads that could fail. | 1 | 1 | 1 | 2 | 1 | 1 |  | 1.1667
Bonneville | Spillway Cranes and Hoists Repiars and Rehab | Modify Spillway Hoist Controls and add a redundant stopping brake. NWP MCIIP #94, Purchase and replace wire ropes on spillway gates and cranes. NWP MCIIP #123
John Day | AWS Rehab Remaining 2 Fish Unit Turbine Pumps (SAP Name: Fish HYD Pumps U1 & U2 Rehabilitiation?) | Age of turbines and possibility of failure leads to requirement for rehab. All 3 installed at same time, one has failed and pump 2 is near failure. One remaining functional pump will likely fail soon. | Critical to the Fish Passage Plan and keep John Day within adult passage criteria under the FCRPS BiOp to provide safe passage for Esa listed fish and resident fish species. The units are more than 50 years old and are currently showing major wear with leaking gearbox seals and worn guide bearings. | 4 | 5 | 5 | 5 | 5 | 5 |  | 4.8333
John Day | North Fish Pump 2 Repair | The JD North Fish Pump 2 needs to be unstacked and repairs are needed to replace the lower guide bearing temperature sensor. | Running the fish pump withougt a working sensor could result in damage to the pump assembly and motor causing the assembly to need a complete overhaul. Fish pumps are need to provide attraction water for the North Fishway at the project. Failure to make the necessary repairs could result in the ladder falling out of passage criteria according to Fish Passage Plan. | 5 | 5 |  | 4 | 4 |  |  | 4.5
John Day | North Fish Pump 4 Repair | The JD North Fish Pump 4 needs to be unstacked and repairs are needed to the lower pump assemblies guide bearing. This is in addition to the replacment that's need to the motors lower bearing assembly which needs replacment. | Fish pumps are need to provide attraction water for the North Fishway at the project. Failure to make the necessary repairs could result in the ladder falling out of passage criteria according to Fish Passage Plan. | 5 | 5 |  | 3 | 4 |  |  | 4.25
John Day | JBS Expansion Joint | Needs to be re-designed for the larger/wider cover plates/ recessed wall to stop water leaks | If the joint fails, the JBS is OOS until repairs can be made. This will result in failure to meet BiOp requirements for safe passage for downstream migrants. | 4 | 4 | 4 | 4 | 4 | 4 |  | 4
John Day | Avian Array Line Replacement | The entire set of avian lines need to be replaced. Inclement weather (high winds, extreme heat, icy condititons, etc.) causes the lines to wear out beyond their expected shelf life, and many of the lines have already failed while the remainding lines could fail at anytime and are at their expected end of life. | Even a few avian lines missing from the grid allows gulls to bypass the remainder of the grid to feed on ESA listed juvenile salmonids. The avian line grid with a full compliment of lines is a requirement under the Fish Passage Plan. | 4 | 4 |  | 4 | 4 |  |  | 4
John Day | Submerged Traveling Screen (STS) Rehab | Submerged Traveling Screen (STS) need major overhaul (corrosion, bearings, etc.). There are 48 working screens plus one extra screen (49 total). | All 49 STSs are overdue for refurbishment. Failure to address the issues could result in significant negative impacts to hydropower production at John Day since turbines can not operate without STS's during the fish passage season (April 1st through December 15th). OPperating turbines without STSs is a violation of the Fish Passage Plan and FCRPS BiOp. | 4 | 3 | 4 | 4 | 5 | 3 |  | 3.8333
John Day | North Fish Ladder HVAC System Replacement | The HVAC system used to cool the north fish ladder pump room needs to be replaced. The system is critical in keeping cool the electrical components, VFD drives and substations for the North fish pumps which provide attraction water to the fish ladder. Increased temperatures during the Summer would likely casue system issues and result in fish passage violations. | Fish pumps are need to provide attraction water for the North Fishway at the project. Failure to replace the HVAC system could result in pump failure and the ladder falling out of passage criteria according to Fish Passage Plan. | 4 | 4 |  | 3 | 4 |  |  | 3.75
John Day | South Fishway Expansion Joint Repair | The south fishway expansion joints are are in need of repair. The majority of these joints start leaking as the weather turns colder. The leaking joints could cause other issues at the ground level with erosion around the suppoot columns of the fishway. | The south fishway (ladder) is critical for adult passage at John Day Dam. Failure of this ladder would limit adult passage to the north fish ladder. Reducing the number of ladders at John Day would reduce the travel time of ESA list fish migrating upstream to natal tributaries to spwan. This delay is a violation of the FCRPS BiOp and the Fish Passage Plan | 3 | 3 |  | 3 | 4 |  |  | 3.25
John Day | South Fish Ladder Section 12 Wall Leak | In this particular location, the fish ladder intersects an abandoned fish ladder. At the junction of the two ladders is a bulkhead slot that has been plugged with concrete. Internal erosion has taken place and is likely still taking place. Further internal erosion could lead to structure foundation undermining which could destabilize the surrounding structures. One possible explanation could be that water is getting into the abandoned fish ladder (from the old entrance possibly?) and is loading the concrete plug in the south fish ladder and eventually leaking through. Ground penetrating radar was used to inspect the area of existing concrete wall to determine concrete integrity. The findings concluded that the concrete in question was of sub-par condition. | Parts of the bulkhead plug have failed and continue to fail. This is a progressive failure in motion. Further failures could lead to debris entering the fish ladder which may require the ladder to be shut down. Additionally, further failures could lead to foundation undermining of structures in the surrounding area. | 3 | 3 | 3 | 3 | 3 | 4 |  | 3.1667
John Day | North Ladder Elevator | The elevator provides safe access and egress for biologists and researchers. | Failure of the elevator puts humans and fish at risk. If the elevator is not working, personnel have to walk up about 12 flights of stairs with a fish bag with fish and water. | 3 | 1 | 3 | 3 | 2 | 2 |  | 2.3333
John Day | Spillway Crane and Gates Rehab, | Develop contract to upgrade the Spillway Crane controls, hoisting equipment, drive system and structure. The Spillway Crane is used for maintenance and emergency installation of stoplogs under gate failures to control the river flow. The rehab would modernize the existing controls making the crane safer and more reliable. The control system is outdated and parts are not available. Control parts must be repaired or invented on site. The hoisting equipment failure rates are increasing due to the high number of duty cycles and operating environment. Crane reliability is decreasing. Out of service durations and occurrences are increasing due to equipment failures from the number of duty cycles and replacement parts not being available. A failure could cause an injury or impact the ability to maintain and operate the Spillway. Crane is required to perform emergency stoplog installations, inspections and maintenance of spillway tainter gates. New top-spill weirs have been installed which causes more frequent use of the crane. Electrical systems have been failing. FY25 E&D $250k, FY26 CT $1.1M. Install four (4) automated Spillway gate Lubrication system using environmentally acceptable lubricants. Trunnion Bushings are failing and require replacement. Gates overstressed due to trunnion friction, possible buckled end frames. The spillway gates operate differently than designed to pass juvenile fish and require more frequent lubrication. The existing system has to be lubricate by hand. Plans and specifications for redesigning the spillway gates braking and gearbox system, re-wiring the controls, upgrading the control system which is incorporated with the GDACS system, and including a farval self lubricating system. There have been frequent failures of gearboxes and multiple cases of the brakes burning up due to sticking closed. Spare parts are now required to be specially built. We also have to remove and send brakes out for refurbishment. Cost of refurbishment is beyond credit card limit, leading to lengthy out of service windows. The controls for the spillway gates are also in poor/antiquated condition.
The Dalles | East exit weirs | Past life expectency. Cavitation becoming unrepairable | Important weirs to control east fish ladder flow. 80% of all passage uses this fishladder. This is for the non-telescoping (154-157). Added to the list with recent engineering opinion. Expect an in depth assessment in winter FY24. | 5 | 5 |  | 4 | 4 |  |  | 4.5 | ranked as if telescoping weirs. Need to reconsider as these are the non-telescoping weirs.
The Dalles | Fishway Automation | Critical components are past useful life and unsupported by OEM. Originally installed fiber optic cable is failing. Replacement parts are no longer available for purchase. Procure and install new fishway automation for all entrance and exit weirs. | This fishway passes approx 80% of total adult fish passage upstream on the Columbia River. If water levels in the fishladder cannot be regulated then fish passage will be negatively impacted. Seven ESA listed salmonid species pass through this system. | 4 | 4 | 4 | 4 | 4 | 5 |  | 4.1667
The Dalles | Fishway Arc Flash Mitigation | Several pieces of equipment have high arc flash incident energies (Cat 4). Arc Flash Hazard Analysis completed in March 2015 by HDR identified several pieces of equipment with high arc flash incident energies. The analysis provided recommended mitigation to lower the arc flash incident energy to a safe level for personnel. The majority of the recommended mitigation is being completed under a power funded contract; however, there is equipment remaining that requires mitigation which can not be power funded. The equipment with high arc flash incident energies are at substations FSQA, FSQ1, FSQ2, FSQ4 and FSQ6. These substations provide power to the fishway (lighting, gate controls, portable pumps, heating, and receptacles). To mitigate the arc flash energy at these locations a maintenance switch and indicating light would be installed providing an input to the protective relay associated with the feed to the substation. During maintenance or switching operations the maintenance mode would be used to lower the arc flash incident energy from category 4 to category 1. | Operations or maintenance on these substations could result in an arc flash accident. An arc flash accident with incident energy of category 4 would result in a serious injury or fatality to the personnel involved. The substation equipment would require replacement due to excessive damage and possible fire. If Maintence switches are not installed, personnel will continue to be at an elevated rist of injury. | 4 | 4 | 4 | 4 | 5 | 4 |  | 4.1667
The Dalles | TDA fishway rockwall stabilization/repair | Basalt walls of both north ladder and south channel degrading with areas of failure. Repair rockfall and stabilize structure. | Major wall failure could block fish passage | 5 | 3 | 4 | 3 | 5 | 5 |  | 4.1667
The Dalles | O&M TD Major Rehab Report | Spillway condition is poor due to continual lack of funding. Spillgates 1-8 are north of the spillwall and heavily relied on for juvenile fish passage. Nine of 15 gates south of spillwall are out of service for various safety concerns. The spillway crane needed for routine maintenance is well beyond service life and cannot be relied on to complete spillgate maintenance. | There are fish passage concerns when spilling south of the spillwall due to the poor eggress hydraulics from the spillgates out of service. If any gates north of the spillwall experienced similar failures, fish passage would be greatly affected since these gates take the vast majority of the juvenile fish passage spill. | 4 | 4 | 3 | 3 | 4 | 5 |  | 3.8333
The Dalles | TDA spillbay 9 trunnion pin | Trunnion pin ceased. Cannot be operated due to potential catastrophic structural failure | Spillwall erosion and potential juvenile fish mortality | 4 | 4 | 3 | 4 | 4 | 4 |  | 3.8333
The Dalles | Count station brush replace | Requires frequent repair. Needs upgrade. | Window not sufficiently cleaned for fish counters to identify species. |  | 3 |  | 3 | 4 |  |  | 3.3333
The Dalles | Fishway Diffuser | Removal of east fishway collection channel unused diffuser valves and permanent closure. Possible removal of east entrance, junction pool, east lower ladder and north ladder diffuser valves and maintain permanently opened. | The Dalles east fishway passes approximately 80% all Columbia river migrating fish, including 7 ESA listed species. Operation of the east fishway auxiliary water system has changed since original design, with the latest fish passage radiotelemtry information. Collection channel valves are always closed due to this changed operation. Maintenance is unnecessary if not used. Permanent closure method is required due to the degraded state of many of these valves. Failure of unused diffuser valves can result in blown diffuser grating resulting in catastrophic fish kill of ESA listed species. | 2 | 2 | 3 | 3 | 3 | 3 |  | 2.6667
The Dalles | Spillway Bay 1 - 9 | Project would complete holistic rehab of gates 1-9. Issues to address include Trunnion Bearings, Structural deficiencies, Mechanical deficiencies and any electrical deficiencies not corrected under Controls project. Engineering and Design in FY24 and Contract in FY25 and FY26.
The Dalles | Spillway Bay 10-23 | Project would complete holistic rehab of gates 10-23. Issues to address include Trunnion Bearings, Structural deficiencies, Mechanical deficiencies and any electrical deficiencies not corrected under Controls project.
The Dalles | Spillway Gantry Crane Rehab/Replacement - Phase 1A/MMR | This crane is 60 plus years old and is in poor condition. The condition results in low reliability and safety concerns. This crane is necessary for deploying stoplogs that are required to support spillway gate repair and maintenance. The crane may also be underrated. It is rated at 30 tons. Design documents specify a 50 ton crane would be required for deploying stoplogs under flow. The project scope also establishes the boundaries of a project, what’s in and what’s out. Included in the scope is the gantry crane and stoplogs. Depending on the results of the alternatives analysis, this equipment may be refurbished or replace with something completely different.
NOAA change in score
All ranking is 1-5, similar to SCT.
NOAA Comment |  | 1 = lowest 5 = highest priority
indicates "defer to Corps"
indicates a missing rank. ODFW has declined to rank items.
Note on F6: Trevor Conder: Unsafe to walk on indicates greater state of failure. Fish in AWS is a problem.