OFFICIAL COORDINATION REQUEST FOR

NON-ROUTINE OPERATIONS AND MAINTENANCE

COORDINATION TITLE- 24BON012 B1 Fish Salvage Operations on Oil Sheen Investigation Units

COORDINATION DATE- 28 May 2024

PROJECT- Bonneville Lock & Dam Powerhouse 1

RESPONSE DATE- 13 June 2023

Description of the problem

Extremely light oil sheens have been observed in the tailrace of Powerhouse 1 (PH1) at Bonneville Lock & Dam over the past year. Please see MFRs 24BON001, 24BON003, 24BON004, 24BON005, 24BON007, and 24BON009 for more details on each event. The type of oil used in the turbines that has been observed in the tailrace is petroleum-based Shell T-68.

The result of the oil sheen observations has caused PH1 Units 2, 3, 4, 5, 6, 7, 8, 9, and 10 to be forced out of service until a thorough oil leak investigation and inspection can occur on each Unit. To perform thorough investigations, inspections, and repairs, each Unit must be dewatered at the start of its investigation period and will remain so until the source of the oil leaks has been properly addressed.

Bonneville currently has two full sets of tail logs and head gates for PH1. Thus, only two Units may be dewatered at a time. A third set of tail logs is currently being rehabbed with the intention of working on three Units, simultaneously. Units 10 and 4 are currently dewatered with tail logs installed. The remaining Units forced out of service must sit without tail logs until the proceeding Units in the priority to fix order are returned to service.

The remaining Unit will be investigated in the following sequence: 9, 3, 6, 5, 8, 7, 2. The estimate for the next Unit (U9) to be dewatered is August 2024.

Per FPP BON Section 5.5.3.: “If a turbine unit has been idle and the draft tube is to be dewatered, it will be operated, when possible, at full load for a minimum of 1 hour, 4 hours preferred. Stop logs will then be placed immediately. It is recommended adjacent Units also be operated for a minimum of 1 hour, 4 hours preferred, to flush fish prior to placing tail logs in the Unit to be OOS.”

This places Bonneville in a unique situation with conflicting goals and requirements; i.e., balancing FPP and fish-related Endangered Species Act (ESA) objectives with Clean Water Act (CWA) spill prevention objectives vs EPA and water quality regulations. Bonneville will proceed forward with the investigation process utilizing one of two possible plans: (1) flush fish per normal FPP required dewatering procedures with the implementation of extensive spill avoidance and minimization measures or (2) place tail logs without running the Unit to flush fish and attempt to salvage all stranded fish. Bonneville has notified the water quality regulators of this dilemma and sought their advice and recommendations. The selection of either of these two plans (or a modified plan) will turn on continuing input from the regulatory and resource agencies. These two plans are described in detail below.

- Follow normal turbine dewatering procedures - run each Unit prior to setting tail logs to flush fish from turbine draft tube.

  - Potential Outcomes:

    - Significantly reduce numbers of fish trapped in turbine draft tube during the dewatering process.

    - Significantly reduce possibility of substantial fish injury or mortality

    - Risk potential discharge of oil into the PH1 tail race.

  - Avoidance and minimization measures to reduce the possible impact of oil discharge:

    - Engage in pre-spill notification to, and coordination with, Action Agencies as well as the U.S. Coast Guard, EPA, ODEQ, and the Washington Department of Ecology.

    - Place oil catching booms in PH1 Tailrace.

    - Stage Bonneville Spill Response Team and equipment downstream of PH1, ready to respond to possible spill.

    - Stage Ranger and utility work boats near tailrace for quick spill response.

    - Stage observers on PH1 tailrace deck to observe for any sheens upon Unit start-up and while running.

    - Shut PH1 Ice and Trash Sluiceway (ITS) when Units closest to the ITS outfall are ran to effectively observe for oil discharge.

- Place tail logs in Units without following procedures to flush fish.

  - Potential Outcomes:

    - Expect significant numbers of fish in Unit’s draft tube. Historical documentation and previous MFRs have detailed numerous occasions that large numbers of sturgeon (tens to thousands of fish) were found in the draft tubes of Units dewatered prior to flushing fish. A main cause of mortality noted in these occurrences was impingement on drains during the dewatering process.

    - Expect significant increase to duration of operation to safely salvage fish from Unit. Increased salvage times and increased time handling fish can adversely affect the health of fish.

    - Increased cost of labor and equipment.

    - Increased safety risk to personnel involved in salvage operations. Removing a single sturgeon from the PH1 draft tubes in an arduous event with precarious removal procedures. The possibility of removing hundreds of sturgeon ranging from 2 feet long to 8 feet long will require new, more technical procedures with greater exposure of risk to personnel. These safety risks include, but are not limited to: lifting of heavy, wet, and thrashing loads; use of technical rope systems; potential to loads overhead; excessive mud/silt/debris buildup in Units causing extremely slippery surfaces; lack of desirable communications within draft tube; risk of operating under new, unproven procedures.

  - Avoidance and minimization measures to reduce these risks:

    - Slowly dewater each Unit. “Burp” the drains to encourage and allow fish to swim away from large grizzly drains on the floor of each draft tube.

    - Significantly increase workforce assigned to salvage operations.

    - Purchase larger “fish salvage” bags to accommodate the potential of fish greater than 5 feet long.

    - Set up considerably more technical rigging devices and systems to extract large fish and large amounts of fish effectively. Complex, seldom used rigging systems expose workers to a greater risk of accident or failure. Increased detail in pre-work safety briefings will help mitigate this risk.

    - Mitigate for heavy debris/silt buildup in the scroll case prior to dewatering draft tube. Following fish removal from the scroll case area, power wash tools can be utilized to clear the scroll case floor and create a safer walking and working environment for rigging operations from above the draft tube.

    - Notify Action Agencies via MOC prior to salvage operations.

Type of outage required: N/A

Impact on facility operation (FPP deviations):

Plan 1:

No deviation from FPP guidance.

	Plan 2:

FPP BON Section 5.5.3.: “If a turbine unit has been idle and the draft tube is to be dewatered, it will be operated, when possible, at full load for a minimum of 1 hour, 4 hours preferred. Stop logs will then be placed immediately. It is recommended adjacent Units also be operated for a minimum of 1 hour, 4 hours preferred, to flush fish prior to placing tail logs in the Unit to be OOS.” If Bonneville is required to follow Plan 2, normal dewatering procedures listed in the FPP would be altered by not running the Units to flush fish prior to placing tail logs.

Impact on unit priority: N/A

Impact on forebay/tailwater operation:

Plan 1:

N/A, other than possibly shutting ITS, placing oil catching booms in tailrace, and staging boats near tailrace.

Plan 2:

N/A

Impact on spill:

Plan 1:

N/A

Plan 2:

N/A

Dates of impacts/repairs:

Present – Fall 2025

Length of time for repairs:

Years

Analysis of potential impacts to fish

Plan 1:

Potential oil exposure to fish in the PH1 tailrace. Decreased downstream migration for juveniles using the ITS for a short amount of time during the running of Units on the South end of PH1.

Plan 2:

Significant increase in handling exposure to fish. Increased risk of fish impingement on draft tube drain. Increased time duration that fish may be trapped within the draft tube due to lengthy, abnormal procedures.

Summary statement - expected impacts on:

Downstream migrants:

Plan 1:

The PH1 ITS must be shut when running Units closest to the ITS Outfall in the PH1 Tailrace in order to properly observe for oil discharge. These short closures of the ITS can increase downstream migration times for fish in the PH1 Forebay. Alternate routes at Bonneville will still be available, including Spillway (during spill season), B2CC (during normal operations), and the DSM2 at PH2. 

Plan 2: 
N/A

Upstream migrants (including Bull Trout):

Plan 1:

N/A

Plan 2:

Adult salmonids migrating upstream are rarely found in draft tubes. If a salmonid travelled into draft tube prior to placing tail logs, these fish would be exposed to the same threats explained above for the sturgeon including, but not limited to: increased handling exposure, increased time trapped within draft tube space, and increased risk of impingement.

Lamprey:
	Plan 1:

N/A

Plan 2:

N/A

Comments from agencies:

Final coordination results:

After Action update (After action statement stating what the effect of the action was on listed species. This statement could simply state that the MOC analysis was correct, and the action went as expected, or it could explain how the actual action changed the expected effect (e.g., you didn’t need to close that AWS valve after all, so there was no impact of the action).  List any actual mortality noted as a result of the action)

Please email or call with questions or concerns.

Thank you,

Jeanette Flemmer
Chief of Fisheries – Bonneville Lock & Dam

541-374-3878

Jeanette.C.Wendler@usace.army.mil