Sent to:   CO

XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX

BON R 071818 1417 CO BON TDA JDA MCN BPA BPC NPD NPC NPP

ATTENTION: BONNEVILLE DAM AND BPA

SUBJECT: PH2 UNIT PRIORITY AND MODIFIED OPERATING RANGE

***********************************************************

CANCEL AND REPLACE CBT: BON R 050818 0849 UNIT 15 MODIFIED

PRIORITY AND OPERATING RANGE

***********************************************************

1. EFFECTIVE IMMEDIATELY, RESUME OPERATING UNIT 15 IN THE

ORDER OF PRIORITY DEFINED IN THE 2018 FISH PASSAGE PLAN (FPP)

TABLE BON-13, AS FOLLOWS:

---PH2 PRIORITY: 11, 18, 12, 17, 13, 14, 15, 16

2. EFFECTIVE IMMEDIATELY THROUGH TUESDAY, JULY 31, 2018,

AT 2359 HOURS, RESTRICT THE OPERATING RANGE OF PH2 UNITS

THAT DO NOT HAVE FLOW CONTROL PLATES TO THE 1% MID-RANGE

(13-15 KCFS). UNITS THAT STILL HAVE FLOW CONTROL PLATES IN

BOTH GATEWELLS A-B MAY BE OPERATED WITHIN THE FULL 1% RANGE.

3. STARTING WEDNESDAY, AUGUST 1, 2018, AT 0001 HOURS, ALL

PH2 UNITS MAY BE OPERATED WITHIN THE FULL 1% RANGE IN

ACCORDANCE WITH THE 2018 FPP SECTION 5.2 (PAGE BON-36).

DURING THIS TIME, PH2 UNITS WILL TYPICALLY BE OPERATED

WITHIN THE 1% MID-RANGE BUT MAY BE OPERATED IN THE FULL

1% RANGE AS NECESSARY TO AVOID DEADBAND ISSUES AT LOWER

FLOWS.

4. THE INTENT OF THIS OPERATION IS TO MINIMIZE TURBULENCE

IN PH2 UNIT GATEWELLS WHERE THE FLOW CONTROL PLATES HAVE

BEEN REMOVED DUE TO FAILURE OF THE ANCHORS. WITHOUT FLOW

CONTROL PLATES, OPERATING PH2 UNITS ABOVE THE 1% MID-RANGE

RESULTS IN EXCESSIVE GATEWELL TURBULENCE THAT ADVERSELY

IMPACTS FISH PASSAGE. THE SCHEDULE FOR REPAIRS IS

CURRENTLY BEING DEVELOPED.

5. THE BONNEVILLE CHAPTER OF THE 2018 FPP WAS MOST RECENTLY

REVISED ON JUNE 14, 2018, AND IS AVAILABLE ONLINE AT:

Blockedhttp://pweb.crohms.org/tmt/documents/fpp/2018/

6. THIS OPERATION WAS REQUESTED BY JON RERECICH (COE-NWP)

AND COORDINATED WITH LISA WRIGHT AND DOUG BAUS (COE-RCC);

SCOTT BETTIN (BPA); ERIN KOVALCHUK (COE-NWP); BEN HAUSMANN

AND COURTNEY NORRISS (COE-BON); AND WITH REGIONAL SALMON

MANAGERS AT THE FPOM MEETING ON JULY 11 AND VIA MEMO OF

COORDINATION (MOC) 18BON04.

7. RCC POINTS OF CONTACT ARE:

---LISA WRIGHT: 503.808.3943 (OFFICE); 503.716.6598 (CELL)

---DOUG BAUS: 503.808.3995 (OFFICE); 503.351.3692 (HOME)

LISA S. WRIGHT

CENWD-PDW-RC

XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX