OFFICIAL NOTIFICATION FOR 

NON-ROUTINE OPERATIONS AND MAINTENANCE

NOTIFICATION DATE-  8 April 2010
PROJECT-  Bonneville Lock and Dam
RESPONSE DATE- No response required, but comments are always welcome.
Description of the problem- Bay 17 still has a broken hoist.  It does not operate automatically and will not be opened at 0001 on 10 April 2010.  Spill for fish passage begins at 0001 on 10 April 2010.  
In addition, flows may be too low to maintain 49 kcfs spill or greater.  Patterns less than 49 kcfs result in gate openings less than 2’ openings.
Type of outage required- Bay 17 will remain closed until at least 12 April.
Impact on facility operation- There will be minimal impact on the facility until Bay 17 needs to be opened.  All other spillgates are automated and GDACS will adjust the openings to maintain spill volume with Bay 17 closed.
Length of time for repairs- Bay 17 will not be repaired this spill season.  
Dog settings are not uniform, nor are they in 6” increments, which is what the spill pattern is set too.  
Under normal flow years, Bay 17 would be dogged at two dogs.  Given the low flow year, and the discussion regarding acceptable spill at BON for the early spring period, it is anticipated Bay 17 will remain closed until flows increase to allow for 50 Kcfs or greater spill.
Expected impacts on fish passage- Fish passage will be impacted more by the low flow spill pattern than by the closure of Bay 17.  Bay 17 affects that pattern, however, GDACS automatically compensates for a closed gate by opening adjacent bays and maintaining the 2’ openings for spill at 50kcfs and above.
Having Bay 17 closed until such time as flows increase or until a suitable dogging position for the gate is determined is not likely to have significant impacts to fish passage.  All other gates are operable and will be operating according to the FPP spill pattern, or compensating for Bay 17.
Comments from agencies

Final results- Bay 17 set at two dogs on 12 April.
Tammy Mackey

NWP Operations Division Fishery Section

Tammy.m.mackey@usace.army.mil 

