OFFICIAL NOTIFICATION FOR 

NON-ROUTINE OPERATIONS AND MAINTENANCE

NOTIFICATION DATE- 20 May 2010

PROJECT-  Bonneville Lock and Dam
RESPONSE DATE- This is a forced outage.  No responses are required, but comments are always welcome.
Description of the problem- BON PH2 Unit 12 is leaking approximately six to ten gallons of oil per day.  The oil is going to the oil/water separator but the Project may not knowingly dump oil into the separator, as per permit specifications.  
The leak must be fixed.  The Project intends to force Unit 12 out of service on 21 May for repairs.  They anticipate the repairs will take one work day if they can replace and vulcanize an o-ring.  If the vulcanization process does not work, the mechanics will need to glue the o-ring and the unit will not return to service until the evening of 22 May.
Type of outage required- Unit 12 forced out of service.
Impact on facility operation- Unit 12 is high in the unit priority list.  The next unit in line is Unit 15.  This will alter the attraction flow for adults and the egress conditions for juveniles passing through the turbines.
Length of time for repair- One work day if the mechanics can vulcanize the o-ring.  If the o-ring must be glued, curing time will prevent the unit from returning to service until the evening of 22 May.
Expected impacts on fish passage- Unit 18 will remain in operation, as will the fish units, but there will be limited attraction flow along the south end of the powerhouse.  
With less than 3000 adult fish passing the project on 19 May, impacts to adults, at this time of year, are expected to be minimal.  All fishways remain open and in criteria, all attraction flow, aside from that provided by Unit 12, will remain in criteria.  Sea lion numbers have decreased so threats from pinnipeds should be less of a concern at this time.
Juvenile passage will remain operational.  With Unit 12 out of service, there will be less turbine flow at the south end of the powerhouse and there may be less guidance to the B2CC, however, the JBS and fish screens will remain operational and within FPP criteria.   

Comments from agencies- 
Final results- Due to the permit violation nature of the oil leak, the Project will move forward with repairs on 21 May.  
Please email or call with questions or concerns.
Tammy Mackey

NWP Operations Division Fishery Section

503-961-5733 Blackberry

Tammy.m.mackey@usace.army.mil 

