OFFICIAL NOTIFICATION FOR 

NON-ROUTINE OPERATIONS AND MAINTENANCE

NOTIFICATION DATE-  04 October 2010
PROJECT-  Bonneville Dam
RESPONSE DATE- No response required, but comments are always welcome.
Description of the problem- DSM2 channel level sensors and the forebay level sensors failed to read water elevations accurately.  A problem was found in the PLC card.  The PLC card could be replaced with the DSM running, however, last time that was attempted orifices and the ERG did not stay in their desired position.  Given that history, Operators and Fisheries decided it would be best to open the ERG to provide the safest and most stable situation for any migrating fish.  The ERG was expected to be open for no more than 5-10 minutes.

On 29 September, Project maintenance attempted to open the ERG.  The ERG failed to open.  This failure caused concern for Operators and Fisheries.  An ERG that fails to open creates a potential flooding or stranding situation for downstream migrants.  
Currently the ERG is in a manual override.  Repairs are expected to occur when parts become available, but no later than this winter maintenance period.  The PLC card was replaced on 30 September.

Type of outage required- No outage was required. 
Impact on facility operation- The JMF was in bypass from the afternoon on 29 September until 30 September.  
The Project has no automatic control over the ERG, there is now a manual override.
Length of time for repairs- The Project took about a day to replace the PLC card.  The ERG remains in manual control.
Expected impacts on fish passage- The ERG never opened so no fish were impacted in that manner.  The JMF was in bypass, so about 100-130 fish went through the bypass side of the JMF.
Comments from agencies- no comments at this time.
Final results- The Project replaced the PLC card and is working on procuring parts for the ERG repairs.
Please email or call with questions or concerns.
Thank you, 

Tammy Mackey

NWP Operations Division Fishery Section

