## LGS-XX No SW EMER (2)
Table LGS-XX. Little Goose Dam Uniform Spill Patterns with No Spillway Weir (Bay 1, 2, and 5 Closed). | [19 empty] | NWW POC - Sean Milligan | Changes for 2016 FPP: | None
Outflow a | Spill b |  | Turbine Unit Outflow (kcfs) c | [6 empty] | No SW Spill Patterns - Gate Stops (#) per Spillbay | [8 empty] | Comments (see footnotes)
(kcfs) | (kcfs) | (%) | 1 d | 2 | 3 | 4 | 5 | 6 | TOTAL | 1 e | 2 | 3 | 4 | 5 | 6 | 7 | 8 | TOTAL |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
11.3 | 0 | 0% | 11.3 | [5 empty] | 11.3 | [8 empty] | 0 |  |  |  | 0 | 0 |  |  | 0 | bar: No SW Spill Patterns - Gate Stops (#) per Spillbay 1 e to No SW Spill Patterns - Gate Stops (#) per Spillbay 2; No SW Spill Patterns - Gate Stops (#) per Spillbay 5
13.0571 | 1.7571 | 13.46% | 11.3 | [5 empty] | 11.3 | [8 empty] | 1 |  |  |  | 0 | 0 |  |  | 0 |  |  | 1.7571 | bar: No SW Spill Patterns - Gate Stops (#) per Spillbay 1 e to No SW Spill Patterns - Gate Stops (#) per Spillbay 2; No SW Spill Patterns - Gate Stops (#) per Spillbay 5; No SW Spill Patterns - Gate Stops (#) per Spillbay 8
14.8143 | 3.5143 | 23.72% | 11.3 | [5 empty] | 11.3 | [8 empty] | 2 |  |  |  | 0 | 0 | 1.7571 |  | 0 |  |  | 1.7571 | bar: No SW Spill Patterns - Gate Stops (#) per Spillbay 1 e to No SW Spill Patterns - Gate Stops (#) per Spillbay 3; No SW Spill Patterns - Gate Stops (#) per Spillbay 5; No SW Spill Patterns - Gate Stops (#) per Spillbay 8
18.0643 | 5.4143 | 29.97% | 12.65 | [5 empty] | 12.65 | x | x | 1 |  | x |  |  | 2 | 3 |  |  |  | 0 | 0 | 1.7571 |  | 0 |  |  | 3.6571
23.8714 | 7.1714 | 30.04% | 16.7 | [5 empty] | 16.7 | x | x | 1 | 1 | x |  |  | 2 | 4 |  |  |  | 0 | 0 | 1.7571 | 1.7571 | 0 |  |  | 3.6571
26.4286 | 8.9286 | 33.78% | 17.5 | [5 empty] | 17.5 | x | x | 1 | 1 | x | 1 |  | 2 | 5 |  |  |  | 0 | 0 | 1.7571 | 1.7571 | 0 | 1.7571 |  | 3.6571
36.1286 | 10.8286 | 29.97% | 14 | 11.3 |  |  |  |  | 25.3 | x | x | 2 | 1 | x | 1 |  | 2 | 6 |  |  |  | 0 | 0 | 3.6571 | 1.7571 | 0 | 1.7571 |  | 3.6571
42.4286 | 12.7286 | 30% | 17.5 | 12.2 |  |  |  |  | 29.7 | x | x | 2 | 2 | x | 1 |  | 2 | 7 |  |  |  | 0 | 0 | 3.6571 | 3.6571 | 0 | 1.7571 |  | 3.6571
48.2857 | 14.4857 | 30% | 17.5 | 16.3 |  |  |  |  | 33.8 | x | x | 2 | 2 | x | 1 | 1 | 2 | 8 |  |  |  | 0 | 0 | 3.6571 | 3.6571 | 0 | 1.7571 | 1.7571 | 3.6571
54.9857 | 16.4857 | 29.98% | 15.9 | 11.3 | 11.3 |  |  |  | 38.5 | x | x | 3 | 2 | x | 1 | 1 | 2 | 9 |  |  |  | 0 | 0 | 5.6571 | 3.6571 | 0 | 1.7571 | 1.7571 | 3.6571
61.5342 | 18.4857 | 30.04% | 17.5 | 14.2485 | 11.3 |  |  |  | 43.0485 | x | x | 3 | 2 | x | 1 | 1 | 3 | 10 |  |  |  | 0 | 0 | 5.6571 | 3.6571 | 0 | 1.7571 | 1.7571 | 5.6571
67.9287 | 20.3857 | 30.01% | 17.5 | 17.5 | 12.543 |  |  |  | 47.543 | x | x | 3 | 2 | x | 1 | 2 | 3 | 11 |  |  |  | 0 | 0 | 5.6571 | 3.6571 | 0 | 1.7571 | 3.6571 | 5.6571
74.2835 | 22.2857 | 30% | 17.5 | 17.5 | 16.9978 |  |  |  | 51.9978 | x | x | 3 | 2 | x | 2 | 2 | 3 | 12 |  |  |  | 0 | 0 | 5.6571 | 3.6571 | 0 | 3.6571 | 3.6571 | 5.6571
80.8917 | 24.2857 | 30.02% | 17.5 | 14.006 | 11.3 | 13.8 |  |  | 56.606 | x | x | 3 | 3 | x | 2 | 2 | 3 | 13 |  |  |  | 0 | 0 | 5.6571 | 5.6571 | 0 | 3.6571 | 3.6571 | 5.6571
87.6033 | 26.2857 | 30.01% | 17.5 | 17.5 | 12.5176 | 13.8 |  |  | 61.3176 | x | x | 3 | 3 | x | 2 | 3 | 3 | 14 |  |  |  | 0 | 0 | 5.6571 | 5.6571 | 0 | 3.6571 | 5.6571 | 5.6571
94.2857 | 28.2857 | 30% | 17.5 | 17.5 | 17.2 | 13.8 |  |  | 66 | x | x | 3 | 3 | x | 3 | 3 | 3 | 15 |  |  |  | 0 | 0 | 5.6571 | 5.6571 | 0 | 5.6571 | 5.6571 | 5.6571
100.7566 | 30.2571 | 30.03% | 17.5 | 17.5 | 17.5 | 17.9995 |  |  | 70.4995 | x | x | 4 | 3 | x | 3 | 3 | 3 | 16 |  |  |  | 0 | 0 | 7.6286 | 5.6571 | 0 | 5.6571 | 5.6571 | 5.6571
107.3716 | 32.2286 | 30.02% | 17.5 | 17.5 | 12.543 | 13.8 | 13.8 |  | 75.143 | x | x | 4 | 3 | x | 3 | 3 | 4 | 17 |  |  |  | 0 | 0 | 7.6286 | 5.6571 | 0 | 5.6571 | 5.6571 | 7.6286
114.1 | 34.2 | 29.97% | 17.5 | 17.5 | 17.3 | 13.8 | 13.8 |  | 79.9 | x | x | 4 | 4 | x | 3 | 3 | 4 | 18 |  |  |  | 0 | 0 | 7.6286 | 7.6286 | 0 | 5.6571 | 5.6571 | 7.6286
120.5331 | 36.1714 | 30.01% | 17.5 | 14.1617 | 11.3 | 13.8 | 13.8 | 13.8 | 84.3617 | x | x | 4 | 4 | x | 3 | 4 | 4 | 19 |  |  |  | 0 | 0 | 7.6286 | 7.6286 | 0 | 5.6571 | 7.6286 | 7.6286
127.0859 | 38.1429 | 30.01% | 17.5 | 17.5 | 12.543 | 13.8 | 13.8 | 13.8 | 88.943 | x | x | 4 | 4 | x | 4 | 4 | 4 | 20 |  |  |  | 0 | 0 | 7.6286 | 7.6286 | 0 | 7.6286 | 7.6286 | 7.6286
133.6488 | 40.1 | 30% | 17.5 | 17.5 | 17.1488 | 13.8 | 13.8 | 13.8 | 93.5488 | x | x | 5 | 4 | x | 4 | 4 | 4 | 21 |  |  |  | 0 | 0 | 9.5857 | 7.6286 | 0 | 7.6286 | 7.6286 | 7.6286
140.1112 | 42.0571 | 30.02% | 17.5 | 17.5 | 17.5 | 17.954 | 13.8 | 13.8 | 98.054 | x | x | 5 | 4 | x | 4 | 4 | 5 | 22 |  |  |  | 0 | 0 | 9.5857 | 7.6286 | 0 | 7.6286 | 7.6286 | 9.5857
146.6613 | 44.0143 | 30.01% | 17.5 | 17.5 | 17.5 | 18.9 | 17.447 | 13.8 | 102.647 | x | x | 5 | 5 | x | 4 | 4 | 5 | 23 |  |  |  | 0 | 0 | 9.5857 | 9.5857 | 0 | 7.6286 | 7.6286 | 9.5857
153.2055 | 45.9714 | 30.01% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 16.9341 | 107.2341 | x | x | 5 | 5 | x | 4 | 5 | 5 | 24 |  |  |  | 0 | 0 | 9.5857 | 9.5857 | 0 | 7.6286 | 9.5857 | 9.5857
157.1286 | 47.9286 | 30.5% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 5 | 5 | x | 5 | 5 | 5 | 25 |  |  |  | 0 | 0 | 9.5857 | 9.5857 | 0 | 9.5857 | 9.5857 | 9.5857
159.1 | 49.9 | 31.36% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 6 | 5 | x | 5 | 5 | 5 | 26 |  |  |  | 0 | 0 | 11.5571 | 9.5857 | 0 | 9.5857 | 9.5857 | 9.5857
161.0714 | 51.8714 | 32.2% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 6 | 5 | x | 5 | 5 | 6 | 27 |  |  |  | 0 | 0 | 11.5571 | 9.5857 | 0 | 9.5857 | 9.5857 | 11.5571
163.0429 | 53.8429 | 33.02% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 6 | 6 | x | 5 | 5 | 6 | 28 |  |  |  | 0 | 0 | 11.5571 | 11.5571 | 0 | 9.5857 | 9.5857 | 11.5571
165.0143 | 55.8143 | 33.82% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 6 | 6 | x | 5 | 6 | 6 | 29 |  |  |  | 0 | 0 | 11.5571 | 11.5571 | 0 | 9.5857 | 11.5571 | 11.5571
166.9857 | 57.7857 | 34.61% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 6 | 6 | x | 6 | 6 | 6 | 30 |  |  |  | 0 | 0 | 11.5571 | 11.5571 | 0 | 11.5571 | 11.5571 | 11.5571
168.9286 | 59.7286 | 35.36% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 7 | 6 | x | 6 | 6 | 6 | 31 |  |  |  | 0 | 0 | 13.5 | 11.5571 | 0 | 11.5571 | 11.5571 | 11.5571
170.8714 | 61.6714 | 36.09% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 7 | 6 | x | 6 | 6 | 7 | 32 |  |  |  | 0 | 0 | 13.5 | 11.5571 | 0 | 11.5571 | 11.5571 | 13.5
172.8143 | 63.6143 | 36.81% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 7 | 7 | x | 6 | 6 | 7 | 33 |  |  |  | 0 | 0 | 13.5 | 13.5 | 0 | 11.5571 | 11.5571 | 13.5
174.7571 | 65.5571 | 37.51% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 7 | 7 | x | 6 | 7 | 7 | 34 |  |  |  | 0 | 0 | 13.5 | 13.5 | 0 | 11.5571 | 13.5 | 13.5
176.7 | 67.5 | 38.2% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 7 | 7 | x | 7 | 7 | 7 | 35 |  |  |  | 0 | 0 | 13.5 | 13.5 | 0 | 13.5 | 13.5 | 13.5
178.6571 | 69.4571 | 38.88% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 8 | 7 | x | 7 | 7 | 7 | 36 |  |  |  | 0 | 0 | 15.4571 | 13.5 | 0 | 13.5 | 13.5 | 13.5
180.6143 | 71.4143 | 39.54% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 8 | 7 | x | 7 | 7 | 8 | 37 |  |  |  | 0 | 0 | 15.4571 | 13.5 | 0 | 13.5 | 13.5 | 15.4571
182.5714 | 73.3714 | 40.19% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 8 | 8 | x | 7 | 7 | 8 | 38 |  |  |  | 0 | 0 | 15.4571 | 15.4571 | 0 | 13.5 | 13.5 | 15.4571
184.5286 | 75.3286 | 40.82% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 8 | 8 | x | 7 | 8 | 8 | 39 |  |  |  | 0 | 0 | 15.4571 | 15.4571 | 0 | 13.5 | 15.4571 | 15.4571
186.4857 | 77.2857 | 41.44% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | x | x | 8 | 8 | x | 8 | 8 | 8 | 40 |  |  |  | 0 | 0 | 15.4571 | 15.4571 | 0 | 15.4571 | 15.4571 | 15.4571
a. At Total Outflow >156 kcfs, spill is >30% due to PH at maximum capacity (~109 kcfs).
b. This table defines spill patterns in increments of one gate stop per row. Spill (kcfs) is calculated as a function of the total number of stops at forebay elevation 633.5 ft (in MOP range 633.0–634.0 ft).
c. Units operated in priority order 1→6 (Table LGS-5) within 1% (Table LGS-6, -7). Unit outflows are estimates of how Unit 1 special operation will work, not precise requirement.
d. Unit 1 manually restricted to upper 1% range (115–125 MW; ~16.0–17.5 kcfs) to disrupt tailrace eddy that forms during spill through SW in Bay 1. Assume Unit 1 is at lower end of the upper 1% range if other units operating uniformly at <16.0 kcfs. Assume all units operating uniformly if average unit discharge is >16.0 kcfs. During low flows (<~38 kcfs), Unit 1 may be operated within full 1% range as necessary (~11.3–17.5 kcfs).
e. SW operating criteria defined in section 2.3.3.7. Flow >85 kcfs = SW-Lo / Flow 50-85 kcfs = SW-Hi / Flow <50 kcfs = SW close.
1 | 1.7571
2 | 3.6571
3 | 5.6571
4 | 7.6286
5 | 9.5857
6 | 11.5571
7 | 13.5
8 | 15.4571
x | 0

## LGS-XX SW EMER
Table LGS-XX. Little Goose Dam Spill Patterns with Spillway Weir in High Crest (SW-Hi) Elevation 622 ft. (Bay 5 Closed). | [20 empty] | NWW POC - Sean Milligan | Changes for 2016 FPP: | None
Outflow a | Spill b |  | Turbine Unit Outflow (kcfs) c | [6 empty] | No SW Spill Patterns - Gate Stops (#) per Spillbay | [8 empty] | Comments (see footnotes)
(kcfs) | (kcfs) | (%) | 1 d | 2 | 3 | 4 | 5 | 6 | TOTAL | 1 e | 2 | 3 | 4 | 5 | 6 | 7 | 8 | TOTAL |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
23.9847 | 7.2 | 30.02% | 16.7847 | [5 empty] | 16.7847 | No SW Spill Patterns - Gate Stops (#) per Spillbay 1 e: SW-Hi; No SW Spill Patterns - Gate Stops (#) per Spillbay 5: x | 0 |  |  |  |  | 7.2 |  |  |  | 0
26.4571 | 8.9571 | 33.86% | 17.5 | [5 empty] | 17.5 | No SW Spill Patterns - Gate Stops (#) per Spillbay 1 e: SW-Hi; No SW Spill Patterns - Gate Stops (#) per Spillbay 5: x; No SW Spill Patterns - Gate Stops (#) per Spillbay 8: 1 | 1 |  | 1 |  |  | 7.2 |  |  |  | 0 |  |  | 1.7571
33.3143 | 10.7143 | 32.16% | 11.3 | 11.3 |  |  |  |  | 22.6 | No SW Spill Patterns - Gate Stops (#) per Spillbay 1 e: SW-Hi; No SW Spill Patterns - Gate Stops (#) per Spillbay 2: 1; No SW Spill Patterns - Gate Stops (#) per Spillbay 5: x; No SW Spill Patterns - Gate Stops (#) per Spillbay 8: 1 | 2 |  | 1 |  |  | 7.2 | 1.7571 |  |  | 0 |  |  | 1.7571
42.0398 | 12.6143 | 30.01% | 17.5 | 11.9255 |  |  |  |  | 29.4255 | No SW Spill Patterns - Gate Stops (#) per Spillbay 1 e: SW-Hi; No SW Spill Patterns - Gate Stops (#) per Spillbay 2: 1; No SW Spill Patterns - Gate Stops (#) per Spillbay 5: x; No SW Spill Patterns - Gate Stops (#) per Spillbay 8: 2 | 3 |  | 1 |  |  | 7.2 | 1.7571 |  |  | 0 |  |  | 3.6571
47.8714 | 14.3714 | 30.02% | 17.5 | 16 |  |  |  |  | 33.5 | SW-Hi | 1 |  | 1 | x |  |  | 2 | 4 |  | 1 |  |  | 7.2 | 1.7571 |  | 1.7571 | 0 |  |  | 3.6571
53.7388 | 16.1286 | 30.01% | 15.0102 | 11.3 | 11.3 |  |  |  | 37.6102 | SW-Hi | 1 |  | 1 | x | 1 |  | 2 | 5 |  | 1 |  |  | 7.2 | 1.7571 |  | 1.7571 | 0 | 1.7571 |  | 3.6571
59.6091 | 17.8857 | 30.01% | 17.5 | 12.9234 | 11.3 |  |  |  | 41.7234 | SW-Hi | 1 | 1 | 1 | x | 1 |  | 2 | 6 |  | 1 |  |  | 7.2 | 1.7571 | 1.7571 | 1.7571 | 0 | 1.7571 |  | 3.6571
65.4741 | 19.6429 | 30% | 17.5 | 17.0313 | 11.3 |  |  |  | 45.8313 | SW-Hi | 1 | 1 | 1 | x | 1 | 1 | 2 | 7 |  | 1 |  |  | 7.2 | 1.7571 | 1.7571 | 1.7571 | 0 | 1.7571 | 1.7571 | 3.6571
71.7897 | 21.5429 | 30.01% | 17.5 | 17.5 | 15.2468 |  |  |  | 50.2468 | SW-Hi | 2 | 1 | 1 | x | 1 | 1 | 2 | 8 |  | 1 |  |  | 7.2 | 3.6571 | 1.7571 | 1.7571 | 0 | 1.7571 | 1.7571 | 3.6571
78.1358 | 23.4429 | 30% | 17.5 | 12.093 | 11.3 | 13.8 |  |  | 54.693 | SW-Hi | 2 | 1 | 2 | x | 1 | 1 | 2 | 9 |  | 1 |  |  | 7.2 | 3.6571 | 1.7571 | 3.6571 | 0 | 1.7571 | 1.7571 | 3.6571
84.5429 | 25.3429 | 29.98% | 17.5 | 16.6 | 11.3 | 13.8 |  |  | 59.2 | SW-Hi | 2 | 1 | 2 | x | 2 | 1 | 2 | 10 |  | 1 |  |  | 7.2 | 3.6571 | 1.7571 | 3.6571 | 0 | 3.6571 | 1.7571 | 3.6571
90.7868 | 27.2429 | 30.01% | 17.5 | 17.5 | 14.7439 | 13.8 |  |  | 63.5439 | SW-Hi | 2 | 2 | 2 | x | 2 | 1 | 2 | 11 |  | 1 |  |  | 7.2 | 3.6571 | 3.6571 | 3.6571 | 0 | 3.6571 | 1.7571 | 3.6571
97.0429 | 29.1429 | 30.03% | 17.5 | 17.5 | 17.5 | 15.4 |  |  | 67.9 | SW-Hi | 2 | 2 | 2 | x | 2 | 2 | 2 | 12 |  | 1 |  |  | 7.2 | 3.6571 | 3.6571 | 3.6571 | 0 | 3.6571 | 3.6571 | 3.6571
103.797 | 31.1429 | 30% | 17.5 | 16.2541 | 11.3 | 13.8 | 13.8 |  | 72.6541 | SW-Hi | 3 | 2 | 2 | x | 2 | 2 | 2 | 13 |  | 1 |  |  | 7.2 | 5.6571 | 3.6571 | 3.6571 | 0 | 3.6571 | 3.6571 | 3.6571
110.4603 | 33.1429 | 30% | 17.5 | 17.5 | 14.7175 | 13.8 | 13.8 |  | 77.3175 | SW-Hi | 3 | 3 | 2 | x | 2 | 2 | 2 | 14 |  | 1 |  |  | 7.2 | 5.6571 | 5.6571 | 3.6571 | 0 | 3.6571 | 3.6571 | 3.6571
117.0429 | 35.1429 | 30.03% | 17.5 | 17.5 | 17.5 | 15.6 | 13.8 |  | 81.9 | SW-Hi | 3 | 3 | 3 | x | 2 | 2 | 2 | 15 |  | 1 |  |  | 7.2 | 5.6571 | 5.6571 | 5.6571 | 0 | 3.6571 | 3.6571 | 3.6571
123.7663 | 37.1429 | 30.01% | 17.5 | 17.5 | 17.5 | 18.9 | 15.2234 |  | 86.6234 | SW-Hi | 3 | 3 | 3 | x | 3 | 2 | 2 | 16 |  | 1 |  |  | 7.2 | 5.6571 | 5.6571 | 5.6571 | 0 | 5.6571 | 3.6571 | 3.6571
130.3459 | 39.1429 | 30.03% | 17.5 | 17.5 | 14.803 | 13.8 | 13.8 | 13.8 | 91.203 | SW-Hi | 3 | 3 | 3 | x | 3 | 3 | 2 | 17 |  | 1 |  |  | 7.2 | 5.6571 | 5.6571 | 5.6571 | 0 | 5.6571 | 5.6571 | 3.6571
137.124 | 41.1429 | 30% | 17.5 | 17.5 | 17.5 | 15.8811 | 13.8 | 13.8 | 95.9811 | SW-Hi | 3 | 3 | 3 | x | 3 | 3 | 3 | 18 |  | 1 |  |  | 7.2 | 5.6571 | 5.6571 | 5.6571 | 0 | 5.6571 | 5.6571 | 5.6571
143.9143 | 43.1143 | 29.96% | 17.5 | 17.5 | 17.5 | 18.9 | 15.6 | 13.8 | 100.8 | SW-Hi | 4 | 3 | 3 | x | 3 | 3 | 3 | 19 |  | 1 |  |  | 7.2 | 7.6286 | 5.6571 | 5.6571 | 0 | 5.6571 | 5.6571 | 5.6571
150.3857 | 45.0857 | 29.98% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 15 | 105.3 | SW-Hi | 4 | 4 | 3 | x | 3 | 3 | 3 | 20 |  | 1 |  |  | 7.2 | 7.6286 | 7.6286 | 5.6571 | 0 | 5.6571 | 5.6571 | 5.6571
156.2571 | 47.0571 | 30.12% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 4 | 4 | 4 | x | 3 | 3 | 3 | 21 |  | 1 |  |  | 7.2 | 7.6286 | 7.6286 | 7.6286 | 0 | 5.6571 | 5.6571 | 5.6571
158.2286 | 49.0286 | 30.99% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 4 | 4 | 4 | x | 4 | 3 | 3 | 22 |  | 1 |  |  | 7.2 | 7.6286 | 7.6286 | 7.6286 | 0 | 7.6286 | 5.6571 | 5.6571
160.2 | 51 | 31.84% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 4 | 4 | 4 | x | 4 | 4 | 3 | 23 |  | 1 |  |  | 7.2 | 7.6286 | 7.6286 | 7.6286 | 0 | 7.6286 | 7.6286 | 5.6571
162.1714 | 52.9714 | 32.66% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 4 | 4 | 4 | x | 4 | 4 | 4 | 24 |  | 1 |  |  | 7.2 | 7.6286 | 7.6286 | 7.6286 | 0 | 7.6286 | 7.6286 | 7.6286
164.1286 | 54.9286 | 33.47% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 5 | 4 | 4 | x | 4 | 4 | 4 | 25 |  | 1 |  |  | 7.2 | 9.5857 | 7.6286 | 7.6286 | 0 | 7.6286 | 7.6286 | 7.6286
166.0857 | 56.8857 | 34.25% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 5 | 5 | 4 | x | 4 | 4 | 4 | 26 |  | 1 |  |  | 7.2 | 9.5857 | 9.5857 | 7.6286 | 0 | 7.6286 | 7.6286 | 7.6286
168.0429 | 58.8429 | 35.02% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 5 | 5 | 5 | x | 4 | 4 | 4 | 27 |  | 1 |  |  | 7.2 | 9.5857 | 9.5857 | 9.5857 | 0 | 7.6286 | 7.6286 | 7.6286
170 | 60.8 | 35.76% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 5 | 5 | 5 | x | 5 | 4 | 4 | 28 |  | 1 |  |  | 7.2 | 9.5857 | 9.5857 | 9.5857 | 0 | 9.5857 | 7.6286 | 7.6286
171.9571 | 62.7571 | 36.5% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 5 | 5 | 5 | x | 5 | 5 | 4 | 29 |  | 1 |  |  | 7.2 | 9.5857 | 9.5857 | 9.5857 | 0 | 9.5857 | 9.5857 | 7.6286
173.9143 | 64.7143 | 37.21% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 5 | 5 | 5 | x | 5 | 5 | 5 | 30 |  | 1 |  |  | 7.2 | 9.5857 | 9.5857 | 9.5857 | 0 | 9.5857 | 9.5857 | 9.5857
175.8857 | 66.6857 | 37.91% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 6 | 5 | 5 | x | 5 | 5 | 5 | 31 |  | 1 |  |  | 7.2 | 11.5571 | 9.5857 | 9.5857 | 0 | 9.5857 | 9.5857 | 9.5857
177.8571 | 68.6571 | 38.6% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 6 | 6 | 5 | x | 5 | 5 | 5 | 32 |  | 1 |  |  | 7.2 | 11.5571 | 11.5571 | 9.5857 | 0 | 9.5857 | 9.5857 | 9.5857
179.8286 | 70.6286 | 39.28% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 6 | 6 | 6 | x | 5 | 5 | 5 | 33 |  | 1 |  |  | 7.2 | 11.5571 | 11.5571 | 11.5571 | 0 | 9.5857 | 9.5857 | 9.5857
181.8 | 72.6 | 39.93% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 6 | 6 | 6 | x | 6 | 5 | 5 | 34 |  | 1 |  |  | 7.2 | 11.5571 | 11.5571 | 11.5571 | 0 | 11.5571 | 9.5857 | 9.5857
183.7714 | 74.5714 | 40.58% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 6 | 6 | 6 | x | 6 | 6 | 5 | 35 |  | 1 |  |  | 7.2 | 11.5571 | 11.5571 | 11.5571 | 0 | 11.5571 | 11.5571 | 9.5857
185.7429 | 76.5429 | 41.21% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 6 | 6 | 6 | x | 6 | 6 | 6 | 36 |  | 1 |  |  | 7.2 | 11.5571 | 11.5571 | 11.5571 | 0 | 11.5571 | 11.5571 | 11.5571
187.6857 | 78.4857 | 41.82% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 7 | 6 | 6 | x | 6 | 6 | 6 | 37 |  | 1 |  |  | 7.2 | 13.5 | 11.5571 | 11.5571 | 0 | 11.5571 | 11.5571 | 11.5571
189.6286 | 80.4286 | 42.41% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 7 | 7 | 6 | x | 6 | 6 | 6 | 38 |  | 1 |  |  | 7.2 | 13.5 | 13.5 | 11.5571 | 0 | 11.5571 | 11.5571 | 11.5571
191.5714 | 82.3714 | 43% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 7 | 7 | 7 | x | 6 | 6 | 6 | 39 |  | 1 |  |  | 7.2 | 13.5 | 13.5 | 13.5 | 0 | 11.5571 | 11.5571 | 11.5571
193.5143 | 84.3143 | 43.57% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 7 | 7 | 7 | x | 7 | 6 | 6 | 40 |  | 1 |  |  | 7.2 | 13.5 | 13.5 | 13.5 | 0 | 13.5 | 11.5571 | 11.5571
195.4571 | 86.2571 | 44.13% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 7 | 7 | 7 | x | 7 | 7 | 6 | 41 |  | 1 |  |  | 7.2 | 13.5 | 13.5 | 13.5 | 0 | 13.5 | 13.5 | 11.5571
197.4 | 88.2 | 44.68% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 7 | 7 | 7 | x | 7 | 7 | 7 | 42 |  | 1 |  |  | 7.2 | 13.5 | 13.5 | 13.5 | 0 | 13.5 | 13.5 | 13.5
199.3571 | 90.1571 | 45.22% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 8 | 7 | 7 | x | 7 | 7 | 7 | 43 |  | 1 |  |  | 7.2 | 15.4571 | 13.5 | 13.5 | 0 | 13.5 | 13.5 | 13.5
201.3143 | 92.1143 | 45.76% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 8 | 8 | 7 | x | 7 | 7 | 7 | 44 |  | 1 |  |  | 7.2 | 15.4571 | 15.4571 | 13.5 | 0 | 13.5 | 13.5 | 13.5
203.2714 | 94.0714 | 46.28% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 8 | 8 | 8 | x | 7 | 7 | 7 | 45 |  | 1 |  |  | 7.2 | 15.4571 | 15.4571 | 15.4571 | 0 | 13.5 | 13.5 | 13.5
205.2286 | 96.0286 | 46.79% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 8 | 8 | 8 | x | 8 | 7 | 7 | 46 |  | 1 |  |  | 7.2 | 15.4571 | 15.4571 | 15.4571 | 0 | 15.4571 | 13.5 | 13.5
207.1857 | 97.9857 | 47.29% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 8 | 8 | 8 | x | 8 | 8 | 7 | 47 |  | 1 |  |  | 7.2 | 15.4571 | 15.4571 | 15.4571 | 0 | 15.4571 | 15.4571 | 13.5
209.1429 | 99.9429 | 47.79% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Hi | 8 | 8 | 8 | x | 8 | 8 | 8 | 48 |  | 1 |  |  | 7.2 | 15.4571 | 15.4571 | 15.4571 | 0 | 15.4571 | 15.4571 | 15.4571
-48
a. At Total Outflow >156 kcfs, spill is >30% due to PH at maximum capacity (~109 kcfs).
b. This table defines spill patterns in increments of one gate stop per row. Spill (kcfs) is calculated as a function of the total number of stops at forebay elevation 633.5 ft (in MOP range 633.0–634.0 ft).
c. Units operated in priority order 1→6 (Table LGS-5) within 1% (Table LGS-6, -7). Unit outflows are estimates of how Unit 1 special operation will work, not precise requirement.
d. Unit 1 manually restricted to upper 1% range (115–125 MW; ~16.0–17.5 kcfs) to disrupt tailrace eddy that forms during spill through SW in Bay 1. Assume Unit 1 is at lower end of the upper 1% range if other units operating uniformly at <16.0 kcfs. Assume all units operating uniformly if average unit discharge is >16.0 kcfs. During low flows (<~38 kcfs), Unit 1 may be operated within full 1% range as necessary (~11.3–17.5 kcfs).
e. SW operating criteria defined in section 2.3.3.7. Flow >85 kcfs = SW-Lo / Flow 50-85 kcfs = SW-Hi / Flow <50 kcfs = SW close.
1 | 1.7571
2 | 3.6571
3 | 5.6571
4 | 7.6286
5 | 9.5857
6 | 11.5571
7 | 13.5
8 | 15.4571
SW-Hi | 7.2
x | 0

## LGS-XX SW-LO EMER
Table LGS-XX. Little Goose Dam Spill Patterns with Spillway Weir in High Crest (SW-Hi) Elevation 622 ft. (Bay 5 Closed). | [20 empty] | NWW POC - Sean Milligan | Changes for 2016 FPP: | None
Outflow a | Spill b |  | Turbine Unit Outflow (kcfs) c | [6 empty] | No SW Spill Patterns - Gate Stops (#) per Spillbay | [8 empty] | Comments (see footnotes)
(kcfs) | (kcfs) | (%) | 1 d | 2 | 3 | 4 | 5 | 6 | TOTAL | 1 e | 2 | 3 | 4 | 5 | 6 | 7 | 8 | TOTAL |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
37.2838 | 11.2 | 30.04% | 14.7838 | 11.3 |  |  |  |  | 26.0838 | No SW Spill Patterns - Gate Stops (#) per Spillbay 1 e: SW-Lo; No SW Spill Patterns - Gate Stops (#) per Spillbay 5: x | 0 |  |  | 4.1162 |  | 11.2 |  |  |  | 0
43.1571 | 12.9571 | 30.02% | 17.5 | 12.7 |  |  |  |  | 30.2 | No SW Spill Patterns - Gate Stops (#) per Spillbay 1 e: SW-Lo; No SW Spill Patterns - Gate Stops (#) per Spillbay 5: x; No SW Spill Patterns - Gate Stops (#) per Spillbay 8: 1 | 1 |  | 1 | 4.2 |  | 11.2 |  |  |  | 0 |  |  | 1.7571
49.1143 | 14.7143 | 29.96% | 17.5 | 16.9 |  |  |  |  | 34.4 | No SW Spill Patterns - Gate Stops (#) per Spillbay 1 e: SW-Lo; No SW Spill Patterns - Gate Stops (#) per Spillbay 2: 1; No SW Spill Patterns - Gate Stops (#) per Spillbay 5: x; No SW Spill Patterns - Gate Stops (#) per Spillbay 8: 1 | 2 |  | 1 | 4.3 |  | 11.2 | 1.7571 |  |  | 0 |  |  | 1.7571
55.3143 | 16.6143 | 30.04% | 16.1 | 11.3 | 11.3 |  |  |  | 38.7 | No SW Spill Patterns - Gate Stops (#) per Spillbay 1 e: SW-Lo; No SW Spill Patterns - Gate Stops (#) per Spillbay 2: 1; No SW Spill Patterns - Gate Stops (#) per Spillbay 5: x; No SW Spill Patterns - Gate Stops (#) per Spillbay 8: 2 | 3 |  | 1 | 4.0864 |  | 11.2 | 1.7571 |  |  | 0 |  |  | 3.6571
61.1578 | 18.3714 | 30.04% | 17.5 | 13.9864 | 11.3 |  |  |  | 42.7864 | SW-Lo | 1 |  | 1 | x |  |  | 2 | 4 |  | 1 | 4.1136 |  | 11.2 | 1.7571 |  | 1.7571 | 0 |  |  | 3.6571
67.0286 | 20.1286 | 30.03% | 17.5 | 17.5 | 11.9 |  |  |  | 46.9 | SW-Lo | 1 |  | 1 | x | 1 |  | 2 | 5 |  | 1 | 4.1 |  | 11.2 | 1.7571 |  | 1.7571 | 0 | 1.7571 |  | 3.6571
72.8857 | 21.8857 | 30.03% | 17.5 | 17.5 | 16 |  |  |  | 51 | SW-Lo | 1 | 1 | 1 | x | 1 |  | 2 | 6 |  | 1 | 4.2 |  | 11.2 | 1.7571 | 1.7571 | 1.7571 | 0 | 1.7571 |  | 3.6571
78.8429 | 23.6429 | 29.99% | 17.5 | 12.6 | 11.3 | 13.8 |  |  | 55.2 | SW-Lo | 1 | 1 | 1 | x | 1 | 1 | 2 | 7 |  | 1 | 4.3 |  | 11.2 | 1.7571 | 1.7571 | 1.7571 | 0 | 1.7571 | 1.7571 | 3.6571
85.0429 | 25.5429 | 30.04% | 17.5 | 16.9 | 11.3 | 13.8 |  |  | 59.5 | SW-Lo | 2 | 1 | 1 | x | 1 | 1 | 2 | 8 |  | 1 | 4.5255 |  | 11.2 | 3.6571 | 1.7571 | 1.7571 | 0 | 1.7571 | 1.7571 | 3.6571
91.4684 | 27.4429 | 30% | 17.5 | 17.5 | 15.2255 | 13.8 |  |  | 64.0255 | SW-Lo | 2 | 1 | 2 | x | 1 | 1 | 2 | 9 |  | 1 | 4.3745 |  | 11.2 | 3.6571 | 1.7571 | 3.6571 | 0 | 1.7571 | 1.7571 | 3.6571
97.7429 | 29.3429 | 30.02% | 17.5 | 17.5 | 17.5 | 15.9 |  |  | 68.4 | SW-Lo | 2 | 1 | 2 | x | 2 | 1 | 2 | 10 |  | 1 | 4.5 |  | 11.2 | 3.6571 | 1.7571 | 3.6571 | 0 | 3.6571 | 1.7571 | 3.6571
104.1429 | 31.2429 | 30% | 17.5 | 16.5 | 11.3 | 13.8 | 13.8 |  | 72.9 | SW-Lo | 2 | 2 | 2 | x | 2 | 1 | 2 | 11 |  | 1 | 4.6 |  | 11.2 | 3.6571 | 3.6571 | 3.6571 | 0 | 3.6571 | 1.7571 | 3.6571
110.6429 | 33.1429 | 29.95% | 17.5 | 17.5 | 14.9 | 13.8 | 13.8 |  | 77.5 | SW-Lo | 2 | 2 | 2 | x | 2 | 2 | 2 | 12 |  | 1 | 4.6 |  | 11.2 | 3.6571 | 3.6571 | 3.6571 | 0 | 3.6571 | 3.6571 | 3.6571
117.2429 | 35.1429 | 29.97% | 17.5 | 17.5 | 17.5 | 15.8 | 13.8 |  | 82.1 | SW-Lo | 3 | 2 | 2 | x | 2 | 2 | 2 | 13 |  | 1 | 4.6 |  | 11.2 | 5.6571 | 3.6571 | 3.6571 | 0 | 3.6571 | 3.6571 | 3.6571
123.8429 | 37.1429 | 29.99% | 17.5 | 17.5 | 17.5 | 18.9 | 15.3 |  | 86.7 | SW-Lo | 3 | 3 | 2 | x | 2 | 2 | 2 | 14 |  | 1 | 4.6 |  | 11.2 | 5.6571 | 5.6571 | 3.6571 | 0 | 3.6571 | 3.6571 | 3.6571
130.4429 | 39.1429 | 30.01% | 17.5 | 17.5 | 14.9 | 13.8 | 13.8 | 13.8 | 91.3 | SW-Lo | 3 | 3 | 3 | x | 2 | 2 | 2 | 15 |  | 1 | 4.6 |  | 11.2 | 5.6571 | 5.6571 | 5.6571 | 0 | 3.6571 | 3.6571 | 3.6571
137.0429 | 41.1429 | 30.02% | 17.5 | 17.5 | 17.5 | 15.8 | 13.8 | 13.8 | 95.9 | SW-Lo | 3 | 3 | 3 | x | 3 | 2 | 2 | 16 |  | 1 | 4.6 |  | 11.2 | 5.6571 | 5.6571 | 5.6571 | 0 | 5.6571 | 3.6571 | 3.6571
143.6429 | 43.1429 | 30.03% | 17.5 | 17.5 | 17.5 | 18.9 | 15.3 | 13.8 | 100.5 | SW-Lo | 3 | 3 | 3 | x | 3 | 3 | 2 | 17 |  | 1 | 4.6 |  | 11.2 | 5.6571 | 5.6571 | 5.6571 | 0 | 5.6571 | 5.6571 | 3.6571
150.2429 | 45.1429 | 30.05% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 14.8 | 105.1 | SW-Lo | 3 | 3 | 3 | x | 3 | 3 | 3 | 18 |  | 1 | 4.1 |  | 11.2 | 5.6571 | 5.6571 | 5.6571 | 0 | 5.6571 | 5.6571 | 5.6571
156.3143 | 47.1143 | 30.14% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 4 | 3 | 3 | x | 3 | 3 | 3 | 19 |  | 1 | 0 |  | 11.2 | 7.6286 | 5.6571 | 5.6571 | 0 | 5.6571 | 5.6571 | 5.6571
158.2857 | 49.0857 | 31.01% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 4 | 4 | 3 | x | 3 | 3 | 3 | 20 |  | 1 |  |  | 11.2 | 7.6286 | 7.6286 | 5.6571 | 0 | 5.6571 | 5.6571 | 5.6571
160.2571 | 51.0571 | 31.86% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 4 | 4 | 4 | x | 3 | 3 | 3 | 21 |  | 1 |  |  | 11.2 | 7.6286 | 7.6286 | 7.6286 | 0 | 5.6571 | 5.6571 | 5.6571
162.2286 | 53.0286 | 32.69% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 4 | 4 | 4 | x | 4 | 3 | 3 | 22 |  | 1 |  |  | 11.2 | 7.6286 | 7.6286 | 7.6286 | 0 | 7.6286 | 5.6571 | 5.6571
164.2 | 55 | 33.5% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 4 | 4 | 4 | x | 4 | 4 | 3 | 23 |  | 1 |  |  | 11.2 | 7.6286 | 7.6286 | 7.6286 | 0 | 7.6286 | 7.6286 | 5.6571
166.1714 | 56.9714 | 34.28% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 4 | 4 | 4 | x | 4 | 4 | 4 | 24 |  | 1 |  |  | 11.2 | 7.6286 | 7.6286 | 7.6286 | 0 | 7.6286 | 7.6286 | 7.6286
168.1286 | 58.9286 | 35.05% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 5 | 4 | 4 | x | 4 | 4 | 4 | 25 |  | 1 |  |  | 11.2 | 9.5857 | 7.6286 | 7.6286 | 0 | 7.6286 | 7.6286 | 7.6286
170.0857 | 60.8857 | 35.8% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 5 | 5 | 4 | x | 4 | 4 | 4 | 26 |  | 1 |  |  | 11.2 | 9.5857 | 9.5857 | 7.6286 | 0 | 7.6286 | 7.6286 | 7.6286
172.0429 | 62.8429 | 36.53% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 5 | 5 | 5 | x | 4 | 4 | 4 | 27 |  | 1 |  |  | 11.2 | 9.5857 | 9.5857 | 9.5857 | 0 | 7.6286 | 7.6286 | 7.6286
174 | 64.8 | 37.24% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 5 | 5 | 5 | x | 5 | 4 | 4 | 28 |  | 1 |  |  | 11.2 | 9.5857 | 9.5857 | 9.5857 | 0 | 9.5857 | 7.6286 | 7.6286
175.9571 | 66.7571 | 37.94% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 5 | 5 | 5 | x | 5 | 5 | 4 | 29 |  | 1 |  |  | 11.2 | 9.5857 | 9.5857 | 9.5857 | 0 | 9.5857 | 9.5857 | 7.6286
177.9143 | 68.7143 | 38.62% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 5 | 5 | 5 | x | 5 | 5 | 5 | 30 |  | 1 |  |  | 11.2 | 9.5857 | 9.5857 | 9.5857 | 0 | 9.5857 | 9.5857 | 9.5857
179.8857 | 70.6857 | 39.29% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 6 | 5 | 5 | x | 5 | 5 | 5 | 31 |  | 1 |  |  | 11.2 | 11.5571 | 9.5857 | 9.5857 | 0 | 9.5857 | 9.5857 | 9.5857
181.8571 | 72.6571 | 39.95% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 6 | 6 | 5 | x | 5 | 5 | 5 | 32 |  | 1 |  |  | 11.2 | 11.5571 | 11.5571 | 9.5857 | 0 | 9.5857 | 9.5857 | 9.5857
183.8286 | 74.6286 | 40.6% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 6 | 6 | 6 | x | 5 | 5 | 5 | 33 |  | 1 |  |  | 11.2 | 11.5571 | 11.5571 | 11.5571 | 0 | 9.5857 | 9.5857 | 9.5857
185.8 | 76.6 | 41.23% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 6 | 6 | 6 | x | 6 | 5 | 5 | 34 |  | 1 |  |  | 11.2 | 11.5571 | 11.5571 | 11.5571 | 0 | 11.5571 | 9.5857 | 9.5857
187.7714 | 78.5714 | 41.84% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 6 | 6 | 6 | x | 6 | 6 | 5 | 35 |  | 1 |  |  | 11.2 | 11.5571 | 11.5571 | 11.5571 | 0 | 11.5571 | 11.5571 | 9.5857
189.7429 | 80.5429 | 42.45% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 6 | 6 | 6 | x | 6 | 6 | 6 | 36 |  | 1 |  |  | 11.2 | 11.5571 | 11.5571 | 11.5571 | 0 | 11.5571 | 11.5571 | 11.5571
191.6857 | 82.4857 | 43.03% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 7 | 6 | 6 | x | 6 | 6 | 6 | 37 |  | 1 |  |  | 11.2 | 13.5 | 11.5571 | 11.5571 | 0 | 11.5571 | 11.5571 | 11.5571
193.6286 | 84.4286 | 43.6% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 7 | 7 | 6 | x | 6 | 6 | 6 | 38 |  | 1 |  |  | 11.2 | 13.5 | 13.5 | 11.5571 | 0 | 11.5571 | 11.5571 | 11.5571
195.5714 | 86.3714 | 44.16% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 7 | 7 | 7 | x | 6 | 6 | 6 | 39 |  | 1 |  |  | 11.2 | 13.5 | 13.5 | 13.5 | 0 | 11.5571 | 11.5571 | 11.5571
197.5143 | 88.3143 | 44.71% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 7 | 7 | 7 | x | 7 | 6 | 6 | 40 |  | 1 |  |  | 11.2 | 13.5 | 13.5 | 13.5 | 0 | 13.5 | 11.5571 | 11.5571
199.4571 | 90.2571 | 45.25% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 7 | 7 | 7 | x | 7 | 7 | 6 | 41 |  | 1 |  |  | 11.2 | 13.5 | 13.5 | 13.5 | 0 | 13.5 | 13.5 | 11.5571
201.4 | 92.2 | 45.78% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 7 | 7 | 7 | x | 7 | 7 | 7 | 42 |  | 1 |  |  | 11.2 | 13.5 | 13.5 | 13.5 | 0 | 13.5 | 13.5 | 13.5
203.3571 | 94.1571 | 46.3% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 8 | 7 | 7 | x | 7 | 7 | 7 | 43 |  | 1 |  |  | 11.2 | 15.4571 | 13.5 | 13.5 | 0 | 13.5 | 13.5 | 13.5
205.3143 | 96.1143 | 46.81% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 8 | 8 | 7 | x | 7 | 7 | 7 | 44 |  | 1 |  |  | 11.2 | 15.4571 | 15.4571 | 13.5 | 0 | 13.5 | 13.5 | 13.5
207.2714 | 98.0714 | 47.32% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 8 | 8 | 8 | x | 7 | 7 | 7 | 45 |  | 1 |  |  | 11.2 | 15.4571 | 15.4571 | 15.4571 | 0 | 13.5 | 13.5 | 13.5
209.2286 | 100.0286 | 47.81% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 8 | 8 | 8 | x | 8 | 7 | 7 | 46 |  | 1 |  |  | 11.2 | 15.4571 | 15.4571 | 15.4571 | 0 | 15.4571 | 13.5 | 13.5
211.1857 | 101.9857 | 48.29% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 8 | 8 | 8 | x | 8 | 8 | 7 | 47 |  | 1 |  |  | 11.2 | 15.4571 | 15.4571 | 15.4571 | 0 | 15.4571 | 15.4571 | 13.5
213.1429 | 103.9429 | 48.77% | 17.5 | 17.5 | 17.5 | 18.9 | 18.9 | 18.9 | 109.2 | SW-Lo | 8 | 8 | 8 | x | 8 | 8 | 8 | 48 |  | 1 |  |  | 11.2 | 15.4571 | 15.4571 | 15.4571 | 0 | 15.4571 | 15.4571 | 15.4571
-48
a. At Total Outflow >156 kcfs, spill is >30% due to PH at maximum capacity (~109 kcfs).
b. This table defines spill patterns in increments of one gate stop per row. Spill (kcfs) is calculated as a function of the total number of stops at forebay elevation 633.5 ft (in MOP range 633.0–634.0 ft).
c. Units operated in priority order 1→6 (Table LGS-5) within 1% (Table LGS-6, -7). Unit outflows are estimates of how Unit 1 special operation will work, not precise requirement.
d. Unit 1 manually restricted to upper 1% range (115–125 MW; ~16.0–17.5 kcfs) to disrupt tailrace eddy that forms during spill through SW in Bay 1. Assume Unit 1 is at lower end of the upper 1% range if other units operating uniformly at <16.0 kcfs. Assume all units operating uniformly if average unit discharge is >16.0 kcfs. During low flows (<~38 kcfs), Unit 1 may be operated within full 1% range as necessary (~11.3–17.5 kcfs).
e. SW operating criteria defined in section 2.3.3.7. Flow >85 kcfs = SW-Lo / Flow 50-85 kcfs = SW-Hi / Flow <50 kcfs = SW close.
1 | 1.7571
2 | 3.6571
3 | 5.6571
4 | 7.6286
5 | 9.5857
6 | 11.5571
7 | 13.5
8 | 15.4571
SW-Hi | 7.2
SW-Lo | 11.2
x | 0