CENWW-OD-G							May 5, 2017

MEMORANDUM FOR THE RECORD 17LGS 08 Vertical barrier screen mortality

SUBJECT: Vertical barrier screen mortality

Background

Units 1, 2 were removed from service on scheduled outage May 1, 0900hrs for routine inspection and trash raking. During video inspections of vertical barrier screens (VBS) tears in the mesh were found and the units were kept out of service.  These tears are likely from forebay debris entering the juvenile fish collection system.  Preparation to repair the torn mesh was initiated immediately, however HSS inspection of the bulkhead, along with borrowing of necessary maintenance equipment from another project and procurement of materials extended the duration before actual work could begin until May 4.

We have only an initial report estimating the magnitude of the mortality that may be associated with fish becoming trapped behind the VBS mesh.  In the first torn panel examined, a 55 gallon drum was half full of mortalities.  Additional panels likely have a similar number of mortalities behind the torn VBS screens.  There are a total of eight panels in the gatewell and three gatewells per unit (a, b, and c).  We have torn VBS mesh panels in gatewell 1b, 2a that will all likely contain varying levels of mortality.

Path Forward

A full maintenance crew will be working 12 hr/day until VBS repair work is complete.  Fishery staff will gather mortalities as each panel is removed.  Specific information on the mortalities will be taken by Smolt Monitoring personnel and provided to the Project biologist.  We have no good estimate for the total amount of mortality from all panels at this time, but are suggesting possibly 5,000 smolts.

Today Unit 2 c and Unit 3a, 3b trashracks are being raked and the VBS mesh inspected.  Unit 4 is being derated to operate in the lower 1% range until it can be raked and have the VBS mesh inspected.  By derating the unit, we will minimize the flow through the unit and the amount of fish passing, because we are uncertain about the level of debris buildup on the trashracks and the possibility of another torn VBS panel both of which could cause further fish mortality.  Units 1 – 4 and 6 trashrack raking planned for week of 15 May.  Unit 4 cannot be raked until Unit 1 is brought back in service.

Relevance to Juvenile Fish Outmigration Timing

The 2017 out migration of yearling Chinook salmon is closely following the 10-year passage index with a median passage date of May 4.  The 10-year median passage date for juvenile steelhead is May 7 and the 2017 steelhead migration timing is ahead of 10-year average likely due to earlier hatchery releases in the Clearwater River.  The 10-year median passage date juvenile sockeye is May 20th and the 2017 juvenile sockeye outmigration is following the historical trends.

Other Actions

An emergency contract is being put in place to remove a large mat of debris in the forebay that extends the full length of the powerhouse and approximately 100 feet out.

Summary:  On May 01, units 1 and 2 were removed from service for trash raking and routine inspections.  On May 05, unit 3 underwent the same routine trash raking and inspection.  During video inspections, tears in the vertical barrier screen (VBS) were discovered.  Tears were found in gatewell slots 1A, 1B, 2A and 3B.  Maintenance crews immediately began strategizing and planning repair work.  One crews worked 12 hour days through May 09 and then began working 2 separate crews around the clock in order to restore turbine units to service as soon as possible.  Vertical barrier screens were replaced with new screens in gatewell slots 1B and 2A.  Vertical barrier screen panels located within gatewell slots 1A and 3B were repaired if possible, otherwise they were also replaced.  Unit 1, 2 and 3 returned to service on May 12, 17 and 13, respectively.

Estimated mortalities by species, and origin:

| Clipped Yearling Chinook | Unclipped Yearling Chinook | Clipped Steelhead | Unclipped Steelhead | Total |
| --- | --- | --- | --- | --- |
| 50 | 39 | 1,438 | 273 | 1,800 |

- Species –  Chinook salmon Oncorhynchus tshawytscha and Steelhead Oncorhynchus mykiss

- Origin – Hatchery and Wild

- Length – N/A

- Marks and tags – N/A

- Marks and Injuries found on carcass – N/A

- Cause and Time of Death – Entrapment behind the torn VBS screens in gatewell slots 1A, 1B, 2A and 3B.  Original discovery in gatewell slots 1B and 2A occurred on May 01.

- Future and Preventative Measures – All VBS screens that were torn have been replaced or repaired.  VBS camera inspections occur during unit outages associated with trash raking and also during unit annual maintenance.

|  | OOS Date | OOS Time | RTS Date | RTS Time |
| --- | --- | --- | --- | --- |
| Unit 1 | 05/01 | 08:56 | 05/12 | 01:52 |
| Unit 2 | 05/01 | 09:01 | 05/17 | 15:22 |
| Unit 3 | 05/05 | 08:25 | 5/13 | 10:56 |