OFFICIAL COORDINATION REQUEST FOR 

NON-ROUTINE OPERATIONS AND MAINTENANCE

COORDINATION TITLE- 12LMN01 diesel generator installation

COORDINATION DATE- 
3/13/12

PROJECT- 
Lower Monumental Dam

RESPONSE DATE-    BEFORE 3/15/12
Description of the problem:
  
Lower Monumental is having a new emergency diesel generator installed under a contract.  As part of the installation,  the contractor has to terminate wires on the SQ0 power panel.  These wires are part of the control scheme from the new PLC.  In order to safely terminate the wires,  SQ0 needs to be taken out of service (OOS).  Taking the SQ0 panel out will cut off the power feeds to primary fish equipment.  The loss of power at SQ0 will cause FCQ1 and FCQ2 to go black.  We will lose power to all three fish pumps, control power to SE1, SE2, SE3, NE1, NE2.  The weir gates will only be affected as we will not be able to raise or lower during this time.  All three fish pumps will be OOS for the duration of this work.  There are two drawings attached in a PDF for reference.  The project was aware of station service switching and unit outages for this job. The project was unaware that we would lose the Fish Pumps until recently.  We pulled a bunch of work forward to 2/29 to minimize this outage.  The original thought was that we got all the work done on 2/29, but some terminations were missed.
There are plant outages scheduled for 3/19 to 3/22 for 2 hours a day for this work.  We need to have the output leads for the PLC connected before we get into performance testing of the Diesel Gens and the PLC the week of March 19

Type of outage required:  
We would like to take the system down on 3/15/12 starting at 1200 and going into the evening hours until the work is complete.  We expect to have the equipment back online by 2400 on 3/15/12

Lower Monumental Fish Pumps 1-3

Adjustment controls to SE and NE weirs

Impact on facility operation:  
We will not be able to run the three fishpumps without the power, thus resulting in a loss of adult attraction water to the fish ladders.

SE and NE weir gates will be inspected prior to and following the work.  The weir gates will not be able to move during the outage and may impact adult fish trying to get into the ladder

Length of time for repairs:  
We would like to take the system down on 3/15/12 starting at 1200 and going into the evening hours until the work is complete.  We expect to have the equipment back online by 2400 on 3/15/12

Expected impacts on fish passage: Adult steelhead that have resided in reservoirs are passing upstream to their spawning locations.  Having this outage start at noon, minimizes the impact to these passing migrants.
Comments from agencies

This will be ok.  Wish we could get this sort of thing done earlier in the season though.

thanks

tom lorz

This coordination request for Lower Monumental will shut down the 3 fish pumps which provide the attraction water to the fish ladders, and will occur on March 15, 2012, from 1200 to 2400 hours.  Adult steelhead passage could occur in the morning hours of March 15, but will be delayed in the tailrace later that the day.  Passage could resume in the morning on March 16.  This short delay should not be a problem for the adult steelhead in the Lower Monumental tailrace.  Please let us know if the work goes as planned.  NOAA Fisheries is okay with the short outage.  Thanks coordinating with us.

Bill Hevlin
Final results: Approval to move forward given after receiving above email responses.  (AS)
Thank you,
