OFFICIAL COORDINATION REQUEST 

FOR 

NON-ROUTINE OPERATIONS AND MAINTENANCE

COORDINATION DATE-   Feb 13, 2009
PROJECT-  Lower Granite Dam
RESPONSE DATE-  Feb. 19, 2009
Description of the problem
According to the Fish Passage Plan, Lower Granite Dam is to have all ESBSs lowered and installed by March 24.  The annual navigation lock is scheduled from March 7 to March 21 which requires significant amount of labor and the use of the crane used to lower fish screens.  March 21 falls on a Saturday.  The project plans lower screens in the 4 highest operating priority turbine units by March 24, and complete lowering the remainder of the ESBSs by March 27.      
Type of outage required: 
The two lowest priority turbine units are to be out of service up to 3 days.
Impact on facility operation:
Minimal as there will likely be insufficient river flow to operate 5 or 6 turbine units.  Spillway capacity is more than adequate to meet additional involuntary spill.  Gas cap will not be exceeded.  Planned fish transport and spill operations will not be affected.
Length of time for repairs
Screen lowering in the 2 remaining turbine units expected to take up to 3 days.
Expected impacts on fish passage
Minimal impact expected, as river flow will not likely exceed the combine flow capacity of turbine units 1-4.  The bypass system and adult fishways will be operated in a normal fashion within fish passage plan requirements.  No unscreened turbine units will be operated.
Comments from agencies

Final results:
Please email or call with questions or concerns.
Thank you, 

