PH1 UNIT SLOW ROLL
Auto/Man

Governor Select

Manual

Make sure blades at approx. 16%

Make sure gates at approx. 0%

Start/Stop

Start – governor mode should change to prestart

Auto/Man

Manual Adjust

Move blades to steep

Auto/Man

Blades select

On Cam – blades should go back to flat

Governor mode should go to breakaway 111 seconds after going to prestart
Auto/ Man

Manual Adjust

Raise speed set point to approx. 3% and let the unit start to slowly roll

Slowly raise speed to between 60% and 80% approximately 10 minutes
Auto/Man

Governor Select

Remote Auto – unit will increase speed and excite.
