BONNEVILLE DAM 

[image: image14.jpg]



FISHWAY STATUS ANNUAL REPORT

2009
By

Ben J. Hausmann

Jonathan G. Rerecich

Kasey M. Welch

U. S. Army Corps of Engineers

CENWP-OD-B

Bonneville Lock & Dam

Cascade Locks, OR 97014

(541) 374-4598
31 January 2009
TABLE OF CONTENTS

INTRODUCTION-----------------------------------------------------------------------------------2

Figure 1. Bonneville Lock and Dam----------------------------------------2
FISHWAY OPERATION AND ACTIVITIES----------------------------------------------3-7

Fish Passage Plan (FPP) Violations-----------------------------------------------3


     Table 1.  Fish passage plan violations and percent in criteria------3
STS/VBS Inspections-------------------------------------------------------------------5
Table 2.  STS and VBS Inspections 2008-2009--------------------------5
Zebra Mussels-----------------------------------------------------------------------------5

Avian Abatement Measures-----------------------------------------------------------5

Auxiliary Water System (AWS) Closures-----------------------------------------6
Table 3.  Fish valve closures and closure times-------------------------6
Fish counts---------------------------------------------------------------------------------6
Fishway Temperature Monitoring--------------------------------------------------7
Figure 2.  Daily average temperatures --------------------------------------7
FISH FACILITY AND TURBINE OUTAGES-------------------------------------------8-9
Table 4.  Fish Facility Outages & Maintenance--------------------------8
Table 5.  Fish Unit Outages--------------------------------------------------8
Table 6.  Turbine Outages of at least 24 hours -------------------------9
FISH REMOVAL----------------------------------------------------------------------------------10
RECENT FISHWAY MODIFICATIONS------------------------------------------------11-13
GLOSSARY----------------------------------------------------------------------------------------14
REFERENCES------------------------------------------------------------------------------------15
INTRODUCTION

The 2009 Fishway Status Annual Report for Bonneville Lock and Dam summarizes activities impacting fish at Bonneville from 1 December 2008 through 30 November 2009.
Primarily a summary of weekly reports, this document summarizes all activities affecting fish passage including maintenance outages, dewaterings and recent modifications to fishway components.   This document is required by the Corps of Engineers’ Northwestern Division, as described in the Fish Passage Plan (FPP).  The FPP contains the following reporting requirements:  “The (weekly) reports shall include: any out of criteria situations observed and subsequent corrective actions taken; equipment malfunctions, breakdowns or damage, along with a summary of resulting repair activities; adult fish control calibrations; STS and VBS inspection; any unusual activities which occurred at the project which may affect fish passage.”   Project biologists perform inspections of the fish passage facilities three times per day and seven days per week during fish passage season and three times per day at least three times per week during winter maintenance season as outlined in the FPP. 
The Project includes two powerhouses, a spillway and two navigation locks.  The older of the two navigation locks has not operated since early 1993.  There are four adult fish ladders for upstream migration located at each powerhouse and the north and south ends of the spillway.  There are three Juvenile Bypass Systems (JBS) for downstream migration: an Ice and Trash Sluiceway (ITS) at Powerhouse 1 (PH1), a downstream migration transportation channel (DSM) at Powerhouse Two (PH2), and the corner collector at (B2CC).

[image: image2.jpg]Washington

Second
Powerhouse
G o

¢mriow




Figure 1.  Bonneville Lock & Dam.

FISHWAY OPERATION AND ACTIVITIES

Fish Passage Plan Violations 

Project Fisheries and the control room operators conduct inspections each day during fish passage season, and at least 3 days per week during winter maintenance.  The results of 328 daily fishway inspections, including 9 conducted by National Oceanic and Atmospheric Administration (NOAA) Fisheries, are shown in the following table.  Listed are the FPP violations and the percentage of days the item was in criteria based on Project Biologist’s inspections only.  Items in criteria 100% of the time are not listed.
Table 1.  Fish Passage Plan violations and percent in criteria.

[image: image3.emf]VIOLATION % IN criteria

PH1

Head at PH1 South collection channel entrance 98.5%

Head at PH1 North collection channel entrance 99.7%

PH1 Ice and Trash Sluiceway end gate 98.5%

PH1 Ice and Trash Sluiceway chain gates 80.5%

Depth over weir at Bradford Island  98.5%

Position or Head at FV3-7 97.6%

Position or Head at FV3-9 97.3%

Depth over weir at A-branch 88.7%

A-branch diffusers  FG3-3, FG3-4, FG3-5, FG3-6

99.4%

PH1 collection channel diffusers 1.2%

Depth over weir at B-branch 98.8%

B-branch diffusers 91.2%

B-branch entrance gates  99.7%

B-branch entrance differential 96.0%

Position or Head at FV5-9, FV5-3 or FV5-4 99.7%

PH2

Cascades Island entrance gates  99.1%

Cascades Island diffusers 92.1%

Cascades Island entrance differential 95.7%

Depth over weir at Upstream Migrant Transportation channel 97.9%

Spillway Bays 99.1%

Head or depth: PH2 North Upstream Entrance 90.2%

Head or depth: PH2 North Downstream Entrance 89.6%

Head or depth: PH2 South Upstream Entrance 89.6%

Head or depth: PH2 South Downstream Entrance 89.6%

PH2 velocity meter/collection channel velocity 3.4%

PH2 collection channel floating orifice gate position 16.2%

Position or Head at FV6-9 98.8%

Depth over PH2 weir 67 99.1%

Depth over PH2 weir 38 93.6%

Depth over PH2 weir 37 90.5%

PH2 JBS channel elevation 99.7%

PH2 JBS orifices 95.1%

DSM 2 Airburst system 11.0%

PH2 fish unit F1 99.4%

PH2 fish unit F2 97.9%

Juvenile Monitoring Facility 99.4%

Calibration once a week 94.2%

Inspections by Project Biologists ( 3/week during winter maintenance, 7/week 

during fish passage season) 98.4%


Out of criteria details

The following paragraphs are explanations for items (Table 1) that were out of criteria more than 80% of the reporting year.

At PH1, the velocity meter is placed in an eddy in the slowest part of the collection channel.  Due to this placement, Project Fisheries used the mechanical velocity meter as the primary indicator of velocity.  The mechanical meter was in criteria 100% of the time.  

PH1 Collection Channel diffusers were out of criteria the entire fish passage season.  FG2-19 and FG2-22A failed to open at water-up in 2006.  The collection channel, however, remained within FPP criteria.  These diffusers are scheduled to be repaired during the winter of 2009/2010.

The PH2 velocity meter is found to be reading incorrectly.  The Project is investigating replacement with a mechanical meter.
Due to a broken lifting beam, stab plates were not installed in the four large Floating Orifice Gates (FOG) for single fish unit operation from 12/1/08 until 1/12/09, when the WA shore fishway went out of service.  Sea lion exclusion bars were placed in the 11 operating FOGs on 04 March.  The 12th FOG was removed for maintenance and replaced with a bulkhead for the remainder of the year.
The DSM2 airburst system had a program malfunction the entire year.  Due to a program issue, screens 6 and 9 would not operate in the automatic cycle.  The project compensated for this by utilizing the mechanical screen cleaners and bursting screens manually.  With this combined effort, there was no debris accumulation on the screens.
The Cascades Island (CI) diffusers were operated with a different configuration than previously used due to the installation of the new entrance weir and its affects on ladder hydraulics.  This was part of the CI entrance modification evaluation and is not considered out of criteria.
STS/VBS Inspections

Submersible traveling screen (STS) and vertical barrier screen (VBS) are inspected once a month.  Each STS has a timer that automatically shows elapsed time of operation, with one month of continuous operation equaling 720 hours.  Bonneville uses an underwater video camera to inspect STSs and VBSs simultaneously.  This gives the project the ability to inspect the screens while they are installed and while the unit is running, and has eliminated the need to dip gatewells.  PH2 STSs are installed from the end of February until December 15 in operational units for juvenile fish passage and for adult fallbacks.
Screens were installed in PH1 priority units by early September for adult fallbacks.  Screens were removed on 19 October to facilitate the DSM1 wall removal contract.  All remaining STSs and VBSs for PH1 units have been scrapped. The automated gates were installed in 2009.  The removal of the wall that divides the sluiceway from DSM1, and sloping the floor is scheduled to be completed prior to the 2010 fish passage season.  These improvements will increase survival rates of out-migrating juveniles by providing a more effective surface bypass route.

Table 2.  STS and VBS Inspections 2008-2009
[image: image4.emf]Unit 

STS 

Removal 

Date

STS 

Install 

Date

1 1/7/09 9/15/08 1/7/09

10/19/09 9/2/09 1179

2 10/19/09 8/31/09

3 1/7/09 9/15/08 1/7/09

1128

11 8/26/08 Unit 11 has remained out of service since 12 June 2008 due to rotor cracks.

12 12/16/08 2/26/09 12/17/08 3/30/09 4/29/09 6/2/09 6/30/09 7/27/09 8/24/09 9/24/09 10/29/09 11/23/2009

658 784 572 804 679 527 645 716 789 674

13 12/16/08 2/26/09 12/17/08 3/30/09 4/29/09 6/2/09 6/30/09 7/27/09 8/24/09 9/24/09 10/29/09 11/23/2009

663 748 663 804 676 138 84 137 604 672

14 12/16/08 2/26/09 12/17/08 3/30/09 4/29/09 6/2/09 6/30/09 7/27/09 8/24/09 9/24/09 10/29/09 11/23/2009

665 758 663 807 679 399 127 285 781 674

15 12/17/08 2/25/09 3/30/09 4/29/09 6/2/09 6/30/09 7/27/09 8/24/09 9/24/09 10/29/09 11/23/09

764 665 803 675 504 245 565 789 665

16 12/17/08 2/25/09 12/17/08 3/30/09 4/29/09 6/2/09 10/29/09 11/23/09

6/15/09 8/13/09 688 735 601 242 360 613

17 12/15/08 2/25/09 12/17/08 3/30/09 4/29/09 6/2/09 6/30/09 7/27/06 8/24/09 9/24/09

627 783 665 711 678 308 139 530

18 12/15/08 2/25/09 12/17/08 3/30/09 4/29/09 6/2/09 6/30/09 7/27/09 8/24/09 9/24/09 10/29/09 11/23/2009

425 780 598 813 678 668 664 697 788 674

STS and VBS Inspection Dates and Run Hours Between Inspections


Zebra/Quagga Mussels

Through weekly inspections of the monitoring station at the PH1 and of all dewatered fishways, we have found no indication of zebra or quagga mussel colonization.  It is widely believed that their arrival is inevitable.  The Project stays involved in regional preparation for zebra/quagga mussel arrival by sending project personnel to training and seminars to stay abreast of the latest information concerning these invasive species.  We continue monitoring with hopes that control programs can be initiated at the first indication of the mussel’s arrival in the Pacific Northwest.   
Avian Abatement Measures

Avian lines are strung over the PH1 tailrace, spillway tailrace, PH2 tailrace, and over the B2CC plunge pool.  Four broken avian lines at the B2CC were repaired on 22 September.  They were discovered broken in spring 2008.  All other lines were intact during the fish passage season.  USDA Wildlife Services avian hazing occurred from May through August.  This was done from the tailrace side of the powerhouses, the spillway, and the shoreline.  

Auxiliary Water System (AWS) Closures

The AWSs were closed on several occasions for varying reasons during the 2008-2009 reporting year.  AWS valves were closed for winter maintenance, trashrack cleaning, and remote operated vehicle (ROV) fishway inspections.  Trashracks are usually cleaned multiple times each month with more frequent cleanings during fall and winter season.  Table 3 shows the number of closures and total closure time per fish valve. 

Table 3.  Fish Valve closures and Closure times.  [image: image5.emf]Fish Valve Reason for closure Number of closures Total closure time

FV 1-1 Winter maintenance 1 1 month, 8 days

FV 3-7 Winter maintenance 1 1 month, 8 days

FV 3-9 Winter maintenance 1 1 month, 8 days

FV 4-3 Winter maintenance 1 1 month, 8 days

FV 4-4 Winter maintenance 1 1 month, 8 days

FV 5-3 Winter maintenance 1 1 month, 11 days

FV 5-4 Winter maintenance 1 1 month, 11 days

FV 5-9 Winter maintenance 1 1 month, 11 days

FV 6-9 Winter maintenance 1 1 month, 18 days

FV 1-1 Trashrack cleaning 33 4 days, 4 hours, 4 minutes

FV 3-7 Trashrack cleaning 22 16 hours, 19 minutes

FV 3-9 Trashrack cleaning 30 10 hours, 46 minutes

FV 5-9 Trashrack cleaning 17 6 hours, 34 minutes

FV 6-9 Trashrack cleaning 23 8 hours, 4 minutes

FV 1-1 ROV 2 8 hours, 33 minutes

FV 3-7 ROV 1 6 hours, 20 minutes

FV 3-9 ROV 1 3 hours, 31 minutes

FV 4-3 ROV 2 4 hours, 57 minutes

FV 4-4 ROV 2 4 hours, 57 minutes

FV 5-3 ROV 1 2 hours, 54 minutes

FV 5-4 ROV 1 2 hours, 54 minutes

FV 5-9 ROV 1 2 hours, 54 minutes

FV 4-3 Bay 18 Flushing 1 31 minutes

FV 4-4 Bay 18 Flushing 1 31 minutes

FV 5-3 Bay 2 Flushing 1 35 minutes

FV 5-4  Bay 2 Flushing 1 35 minutes

FV 5-3 CI Entrance Weir Installation 1 39 minutes

FV 5-4  CI Entrance Weir Installation 1 39 minutes


Fish counts

The Corps of Engineers contracts with Washington Department of Fish & Wildlife (WDFW) for all fish counting.  The fish count season is year round with visual counts from March until November and video counts during the rest of the year.  All fish count numbers may be found at http://www.nwp.usace.army.mil/op/fishdata/home.asp
Fishway Temperature Monitoring
Project biologists monitor fishway temperatures throughout the fish passage season, from March through November.  The Adult Fish Facility (AFF) and Juvenile Monitoring Facility (JMF) are monitored primarily during the summer months when high temperatures can result in the need for sampling restrictions to minimize impact on fish passage.  In 2009, temperatures were monitored from May through September.  The following temperature charts illustrate daily average temperature trends.  Detailed daily temperatures may be found in our weekly reports.  
For much of the 2009 fish passage season, all four temperature probes experienced technical difficulties.  As a result, only temperatures collected from Bradford Island and the AFF are displayed. New probes are scheduled to be installed prior to the 2010 passage season.  
[image: image1.png]


[image: image6.emf]Daily average temperatures

30

40

50

60

70

80

1-Mar

1-Apr 1-May 1-Jun 1-Jul 1-Aug 1-Sep

1-Oct

1-Nov

Degree F

Bradford Island AFF



FISH FACILITY AND TURBINE OUTAGES
Table 4.  Fish Facility Outages of at least 12 hours.

[image: image7.emf]Fish Facility Date Out of Service Date in Service Reason for Outage

BI Lamprey Ramp 04 Nov 09 26 May 09 Winter Maintenance

WA Shore Lamprey Ramp 04 Nov 09 26 May 09 Winter Maintenance

CI Lamprey Ramp 08 Sep 09 26 May 09 Winter Maintenance

Cascades Island Exit 20 Jan 09 09 Jan 09 Winter Maintenance - UMT closure

Cascades Island ladder 20 Jan 09 28 Feb 09 Winter Maintenance

UMT 09 Jan 09 28 Feb 09 Winter Maintenance

JMF 31 Oct 08 02 Mar 09 System in bypass for winter

JMF 30 Oct 09 Present System in bypass for winter

B2CC 01 Sep 08 03 Apr 09 Closed for Winter Maintenance until 2009 fish passage season.

B2CC 01 Sep 09 Present Closed for Winter Maintenance until 2010 fish passage season.

Bradford Island Ladder 03 Dec 08 09 Jan 09 Winter Maintenance

PH1 ITS 02 Nov 09 Present Facitilitate DSM1 wall removal contract.

DSM 1 19 Oct 09 N/A DSM 1 wall removal

DSM 1 15 Jan 09 31 Aug 09 Open and running south for Kelt passage

DSM 2 18 Dec 08 24 Feb 09 Winter Maintenance

WA Shore Ladder 12 Jan 09 28 Feb 09 Winter Maintenance

AFF 05 Jan 09 20 Apr 09 Winter Maintenance

ITS 17 Feb 09 02 Mar 09 Automated chain gate installation in 3B, 6C, and 10B.


Table 5.  Fish Unit Outages and Reduced Loads.

[image: image8.emf]Dates Fish Unit 1

12/1/2008 - 2/28/09 OOS for Annual Maintenance, WA shore ladder outage

04/15/09 OOS from 2002 until 2321 for T11 wiring/BPA trip test

04/27/09 OOS from 1414 until 1526 due to transformer trip

08/04/09 OOS for slip ring maintenance and fishway ROV inspection from 0305 until 1606

Dates Fish Unit 2

12/31/08 On standby to facilitate U17 and U18 trash raking

01/08/09 On standby for F1 testing

1/10/09 - 3/4/09 OOS for Annual Maintenance, WA shore ladder outage

4/16/2009 - 4/17/2009 OOS for T12 wiring/BPA trip test from 1956 16 April until 0042 17 April.

04/27/09 OOS from 1414 until 1719 due to transformer trip

05/30/09 OOS from 1546 until 1841 due to emergency shutdown and 59G relay replacement

06/23/09 OOS from 0323 until 0742 due to breaker issues

08/04/09 OOS from 0305 until 1606 for slip ring maintenance and fishway ROV inspection

11/05/09 OOS from 1233 until 1423 for trashrack raking


Fish units 1 and 2 were placed on standby at other times during the year to “float” trash away from the trash racks.  When drawdown measured one foot or greater, fish units were shut down. An adjacent unit was then operated to pull trash away from the fish unit trashracks.  This procedure helped prevent debris and silt from accumulating in front of the fish units.  Most of the unit outages associated with the floating of trash and debris occurred between 2400 and 0300 to minimize impact on adult fish passage.
Table 6.  Turbine Outages of at least 24 hours. [image: image9.emf]Turbine Unit Date Out Date In Reason for Outage

7 04 Jun 07 Turbine rehab

11 12 Jun 08 Rotor cracks

9 04 Aug 08 Turbine rehab

15 05 Sep 08 17 Dec 08 Rotor pole failure

8 04 Dec 08 06 Dec 08 Current transformer (CT) installation

17 07 Dec 08 08 Dec 08 Damaged STS plug

8 17 Dec 08 24 Mar 09 Lower guide bearing failure

10 05 Jan 09 07 Jan 09 Hot bearing, high drawdowns

12 14 Jan 09 20 Jan 09 Headgate change out

1 30 Jan 09 31 Jan 09 CT replacement

15 18 Mar 09 19 Mar 09 Governor leak

0 07 Apr 09 09 Apr 09 Semi-annual maintenance

12 09 Apr 09 13 Apr 09 Exciter trouble

8 13 Apr 09 15 Apr 09 Bank 7/8 outage

2 05 May 09 06 May 09 Annual maintenance

17 04 May 09 08 May 09 Headgate change out

16 09 May 09 30 Sep 09 Exciter trouble, grounding issue

10 13 May 09 14 May 09 Annual maintenance

8 18 May 09 21 May 09 Bank 7/8 outage

10 05 Jul 09 09 Jul 09 Bank 9/10 outage

6 13 Jul 09 09 Sep 09 Five year overhaul

3 19 Jul 09 23 Jul 09 Annual maintenance and Bank 3/4 bi-annual service

4 19 Jul 09 23 Jul 09 Bank 3/4 bi-annual service

5 02 Aug 09 06 Aug 09 Bank 5/6 bi-annual serivce

8 02 Aug 09 03 Aug 09 CT work

1 10 Aug 09 13 Aug 09 Bank 1/2 maintenance

12 10 Aug 09 11 Aug 09 Annual maintenance

14 16 Aug 09 19 Aug 09 Annual maintenance

15 19 Aug 09 20 Aug 09 Annual maintenance

3 20 Aug 09 22 Aug 09 Install crow's nest

2 24 Aug 09 26 Aug 09 Cooling water pump replacement

18 24 Aug 09 25 Aug 09 Annual maintenance

3 14 Sep 09 15 Sep 09 Bank 3/4 testing

4 14 Sep 09 05 Nov 09 Five year overhaul

17 26 Sep 09 28 Sep 09 Exciter trouble

17 05 Oct 09 30 Nov 09 Four year overhaul

0 19 Oct 09 21 Oct 09 Semi-annual maintenance

3 01 Nov 09 02 Nov 09 Main breaker wouldn't close

8 05 Nov 09 14 Nov 09 DSM1 orifice removal

10 16 Nov 09 21 Nov 09 DSM1 orifice removal

3 19 Nov 09 08 Dec 09 Bank 3/4 loss

4 19 Nov 09 08 Dec 09 Bank 3/4 loss

6 21 Nov 09 30 Nov 09 DSM1 orifice removal



FISH REMOVAL
Fish passage facilities and turbine units are taken out of service and dewatered to allow for inspection, preventative maintenance, repairs, and modifications.  As facilities and turbine units are dewatered, project biologists, outside agency personnel, and other project personnel follow procedures outlined in the Fish Passage Plan and detailed in the Fish Salvage Plan to minimize impacts on fish.  Fish recovered are typically released into the forebay above the new navigation lock. Salvaged sturgeon and juvenile salmonids, however, are released below the dam at Hamilton Island.  The following is a summary of the number of fish that were removed during facility and turbine unit dewaterings.  All fish were recovered in good condition unless otherwise noted.

Bradford Island (12/03/2008): two adult coho, two adult steelhead, 14 juvenile steelhead,  four juvenile chinook, one sculpin, 22 whitefish/peamouth/suckers (residents), one catfish, one crawdad, 100 juvenile shad, one lamprey.

Bradford Island Junction Pool (12/03/2008):  two adult steelhead, 53 juvenile steelhead, 10 juvenile chinook, three lamprey, 12 sturgeon (3’-8’), one adult shad, twenty four juvenile shad, fifty four resident fish.

AFF (1/5/2009):  two juvenile chinook, one juvenile steelhead, one peamouth, one sturgeon, 25 suckers.  Fish were released in the Washington Shore ladder.
Washington Shore Fishway (1/12/2009): 32 clipped adult steelhead, six unclipped adult steelhead, one chinook jack, one lamprey ammocete, three smallmouth bass, two stickleback, one sculpin, 37 residents (including peamouth, pikeminnow, whitefish, suckers).

DSM 1 (1/15/2009):  13 juvenile steelhead, one juvenile chinook, 15 stickleback, five bass, one sculpin, one sucker.
Cascades Island (1/20/2009): five clipped juvenile steelhead, one unclipped juvenile steelhead, one juvenile chinook, three sculpin, approximately 100 stickleback, one bass, one sucker, one whitefish, one peamouth, three crayfish, one dead unclipped juvenile steelhead. 

Upstream Migrant Transportation channel (UMT) (1/20/2009): one clipped adult steelhead, three juvenile steelhead, two sculpin and five stickleback.

Cascades Island diffuser pools, FG6-5 through FG6-10(1/22/2009): eight adult steelhead.

Cascades Island entrance (1/23-24/2009): 400-500 sturgeon, six peamouth, one dead clipped adult steelhead, one dead sturgeon.
AFF valve 14 drain chamber (1/27/2009):  two adult clipped steelhead, one juvenile steelhead, one juvenile chinook.

South Monolith (2/3/2009): 30 sturgeon.

PH2 PCC AWS conduit (2/4/2009): eight sturgeon, one of which is likely to be a mort.

Units 12 and 14 gatewells (2/11/09): 100 juvenile lamprey (macropthalmia), two bluegill, five stickleback, one pumpkinseed, one crappie.

North Monolith (2/17/09 and 2/18/09): one lamprey ammocoete, two sturgeon, and two suckers.

PH2 AWS conduit – North section (2/18/09): four juvenile chinook, four sturgeon, one adult lamprey, 29 sculpin, 10 suckers, one bass, six stickleback, and one crawdad.

PH2 PCC Diffuser C-5 (2/25/09): 48 sturgeon.

Upstream navlock gate (3/9/09): five juvenile chinook, one juvenile steelhead.

DSM1 (3/24/09): one juvenile unclipped steelhead, two juvenile bass, one stickleback.

Gatewell 17C (5/4/09): 500 juvenile yearling, sub-yearling chinook, and steelhead.

Unit 6 draft tube (7/14/09): one lamprey.

Unit 16 draft tube (8/18/09): five sturgeon, one carp, one catfish.

Unit 6 tail logs (9/3/09): 13 sculpin, 12 crawdads.

Unit 4 draft tube (9/15/09): one sturgeon.

Unit 16 tail logs (9/25/09): 12 sculpin, two catfish, one crawdad.

Gatewell 17A (10/5/09): thousands of juvenile shad.

Unit 17 draft tube (10/6/09): 23 sturgeon, two catfish, five bullhead.

DSM 1 (10/19/09): four crawdads, one sculpin.

Unit 4 tail logs (10/30/09): Two suckers, 24 sculpin, 36 crawdads, three bass, one bluegill.

AFF entrance, exit and under brail pool (11/9/09): six steelhead and three unknown salmon.

Unit 17 tail logs (11/24/09):  52 sculpin, two crawdads, one catfish, one sturgeon.
Fishway Modifications (1996-Winter 2008/09)
POWERHOUSE ONE ADULT
2006-present.  Sea lion exclusion devices (SLEDs) are installed at the fishway entrances to prevent sea lion access to the fish ladder.
2005/06.  Bulkheads were installed in the orifice gate and telescoping gate slots.  Gates were removed along with the associated electronic and mechanical equipment.

2005/06.  Passive Integrated Transponder (PIT) tag detectors installed in four serpentine weirs in the Bradford Island fishway.

2004-present. Utilize ROVs for fishway inspections instead of divers.

2003/04.  Installed new electronic velocity meter at the north end of the PH1CC.
2002/03.  PH1CC orifice gates and telescoping gates are closed and disabled.  Studies indicated more fish exited these gates than entered.  Weir gates were left in service.

2001/02.  Extra orifices in the overflow weirs were filled with concrete.

2000/01.  PIT tag detectors installed in four orifice weirs in A-branch and four orifice weirs in 
B-branch.
1998/99.  FG3-10 through 17 disabled and filled with concrete.  FG3-14 (at the junction pool) covered with metal plates instead of concrete.
POWERHOUSE ONE JUVENILE
2009- present.  Removal of the wall separating DSM1 from the ITS begins.  All remaining PH1 screens scrapped.
2008/09.  ITS automated chaingates installed in 3B, 6C, and 10B.

2004-2007. DSM1 is disabled as a juvenile bypass route.  Screens are not installed during fish passage season except from 15 September until 15 December for adult fallback.  DSM1 runs south during this time.
2001-2003. Unit 8 extended submerged bar screens were deemed undesirable and replaced with standard STSs.

2001-present.  The 2000 Biological Opinion (BiOp) required the removal of impediments to fish passage from the turbine environments.  Removal and replacement of excess metal, with fish friendly alternatives, occurs as units go out of service for rehab.

2000-present. Turbine rehab involves installing minimum gap runners on all PH1 main units.  Roughly one unit is completed each year.  Units 1-6, 8, and 10 are completed.  Units 7 and 9 will be finished in 2010.
POWERHOUSE ONE LAMPREY
2005/06.  PIT tag detection and expanded lamprey ramp installed in the Bradford Island FV3-9 AWS channel.

2003/04.  Lamprey ramp installed in the Bradford Island FV3-9 AWS channel.

CASCADES ISLAND FISHWAY/ UMT
2004-present.  Utilize ROVs for fishway inspections instead of divers.

2004/05.  UMT fish count window crowder and window cleaner removed.

2001/02.   New diffuser covers built and installed.

2000/01.  More PIT tag detectors installed in four orifice weirs.

1999/00.  FG6-1 through 4 filled in with concrete.

1998/99.  PIT tag detectors installed in four orifice weirs.
1996-2000. The UMT drain is blind flanged and no longer used.

CASCADES ISLAND LAMPREY
[image: image10.wmf]0

5000

10000

15000

20000

25000

03/15/05

03/30/05

04/14/05

04/29/05

05/14/05

05/29/05

06/13/05

06/28/05

07/13/05

07/28/05

08/12/05

08/27/05

09/11/05

09/26/05

10/11/05

10/26/05

Date

Number of Fish

Chinook

Steelhead

Sockeye

Coho

2008/09.   Lamprey ramp and bollards installed in CI entrance pool.  Variable width entrance weir installed in May. 
[image: image11.jpg]


 2005/06.  Half duplex PIT tag detectors were installed along the picket leads to track lamprey.

POWERHOUSE TWO ADULT
2008/09  Picket leads installed perpendicular to existing AFF picket leads.
[image: image12.jpg]


2007/08   Manufactured new FOG SLEDs.
2006/07.  Installed new staff gauges in the monoliths.
2006/07.  AFF lamprey orifice gate removed due to pulley failure resulting in salmon passage blockage and dewatering difficulties.
2005-present.  SLEDs installed at fishway entrances to prevent sea lion access to the fish ladders.
2005/06.  AFF count window crowder removed due to structural failure.

2004-present.  Utilize ROVs for fishway inspections instead of divers.

2004/05.  Repaired the AWS conduit.

[image: image13.jpg]R L

L




2004/05.  Installed new velocity meter at South Upstream Entrance (SUE).  
2004/05.  PIT tag detectors installed in four serpentine weirs.

2004/05.  AFF brail pool modifications made.  The brail pool is now the primary recovery pool.

2003/04.  AFF electrical upgrades complete.

2003/04.  Picket leads for the triangle section were removed.

2002/03.  Removed old metal staff gauge frames from monolith entrances.
2001/02.  PIT tag detectors installed in eight orifice weirs, four upstream and four downstream of the AFF.
1999/00.  AFF exit ladder equipped with orifice PIT tag detectors.

POWERHOUSE TWO JUVENILE
2008/09.   Release pipe attached to JMF outfall pipe for juveniles trucked from Walla Walla District.
2007/08.   Behavioral Guidance Structure (BGS) installed in PH2 forebay.
2007/08.   PH2 Downstream Migrant transportation channel (DSM2) LED lights returned to halogen lights due to the unknown effects of LEDs. 
2007/08.  Units 14 and 18 are modified for new VBSs and improved FGE.
2006/07.  New LED lights replace the halogen lights.  The LED lights are cooler and will last years longer than the halogens.  These lights were salvaged from DSM1.

2006/07.  Units 11, 15, 16 are modified for new VBSs and improved FGE.

2005/06.  B2CC PIT tag antenna installed.

2005/06.  SMF full flow PIT tag antenna installed. 
2005/06.  Units 12 and 13 modified for new VBSs and improved Fish Guidance Efficiency (FGE).

2004/05.  VBS modifications for Unit 17 result in screen failure.  The design for the new VBSs is re-examined and redrawn.
2004/05.  SMF Outfall hydrocannon piping is replaced.
2004/05.  B2CC complete and online.
2003/04.  Unit 17 VBSs and gatewells are modified to improve FGE.  Modifications include gap closure devices on the STSs and modified VBSs.

2002/03.  NOAA Fisheries fyke net frame is removed from the tailrace.

2002/03.  Unit 15 gatewells are partially modified to improve FGE.  Modifications include gap closure devices on the STSs.
2002/03.  Biologists noticed places of ovality while inspecting the two mile pipe.  The pipe has been monitored regularly to document potential changes. 

2002-present.  The 2000 BiOp required the removal of impediments to fish passage from the turbine environments.  Removal and replacement of excess metal, with fish friendly alternatives, occurs as units come out of service for maintenance.

2001/02.  Raised the DSM2 walkway grating to prevent fish from impacting it.
2001/02.  Modified the DSM2 add-in screen to vertical bars to allow juveniles to move out of the add-in water and into the channel.  The bars didn’t reach the walkway so a perforated plate was added later in the season to prevent adults from jumping into the add-in section.
2001/02.  Flume covers were added over the switchgates.  This was to encourage fish to stay in the main channel and not seek shade by swimming under the switchgates.

2000/01.  Saltwater rearing moved into the SMF.  

2000/01.  Modifications were made to the primary dewatering structure drain pipe to divert more water into the wetlands.  This reduced the flow fluctuations and air bubbles under the perforated plate in the primary dewatering structure.

1998-2000. SMF construction completed.  The facility goes online.  

POWERHOUSE TWO LAMPREY
2007/08.  Lamprey ramp installed in the Washington Shore FV6-9 AWS channel.
2004/05.  Lamprey ramp installed at North Downstream Entrance (NDE).  
2000/01.  Lamprey plates are installed over the Washington Shore diffuser grates.

BASS LAKE
2006.  The leaking drain is repaired.  The lake holds water and coho are seen spawning in the outlet (Moffett Creek) of Bass Lake.  The salvaged logs create log jams over the sink hole.
2004.  Salvaged logs are placed in Bass Lake to provide habitat. 

GLOSSARY
AFF-----
Adult Fish Facility.  Lab associated with the Washington Shore ladder.  Adult fish are trapped for research purposes.

AWS-------------------------Auxiliary Water Supply.  

B2CC------------------------Powerhouse Two Corner Collector.  A surface bypass system located in the southern corner of the Bonneville Second Powerhouse forebay.  

BGS--------------------------Behavioral Guidance Structure.  Located in the PH2 forebay.
BI---
Bradford Island Fishway

BiOp
Biological Opinion.

CI--
Cascades Island Fishway

Collection Channel(CC)
Part of the adult fishway spanning the length of the downstream side of each powerhouse.

DSM1
Downstream Migrant transportation channel (PH1).  Transport channel for adult fallback and steelhead kelts from gatewell orifices to the ice and trash sluiceway.  

DSM2
Downstream Migrant transportation channel (PH2).  Transport channel for juvenile fish from gatewell orifices to the juvenile transport pipe. 

FG
Fish diffusion gate.
FGE--------------------------Fish Guidance Efficiency.

FOG
Floating Orifice Gate.
Forebay
That area of a reservoir immediately upstream of a dam.

FPP
Fish Passage Plan.

FV
Fish Valve.

ITS
Ice and Trash Sluiceway.

JBS
Juvenile Fish Bypass System.
JMF--------------------------Juvenile Monitoring Facility.  Lab associated with the PH2 JBS.  

NDE-----
North Downstream Entrance.  Refers to one of the four large overflow weir adult fishway entrances at PH2.

NUE
North Upstream Entrance.  See NDE.

NOAA
National Oceanic and Atmospheric Administration.

OOS
Out of Service.

PH1
Bonneville Powerhouse One.

PH2
Bonneville Powerhouse Two.

PIT ------
Passive Integrated Transponder.  A tag inserted into juvenile and adult fish.  Detectors are installed at all fish passage systems.

Project
Bonneville Lock & Dam.

ROV--------------------------Remotely Operated Vehicle.

SDE
South Downstream Entrance.  See NDE.

SLED
Sea Lion Exclusion Device

SUE
South Upstream Entrance.  See NDE.

STS
Submersible Traveling Screen.

Tailrace
The portion of a river immediately downstream of a dam or powerhouse.

UMT-----
Upstream Migrant Transportation channel.  This channel connects Cascades Island ladder to Washington Shore ladder through PH2.

VBS
Vertical Barrier Screen.

WDFW
Washington Department of Fish & Wildlife.

References
2008.  Fish Passage Plan for Corps of Engineers Projects.  U. S. Army Corps of Engineers, Northwestern Division, Portland, Oregon.

2009.  Fish Passage Plan for Corps of Engineers Projects.  U. S. Army Corps of Engineers, Northwestern Division, Portland, Oregon.  

2008-2009. Weekly reports for Bonneville Dam.  U.S. Army Corps of Engineers, Portland District.  Bonneville Lock and Dam.

2008-2009. Daily fishway inspections for Bonneville Dam.  

Figure 2.  2009 Bonneville Fishway temperatures.








� EMBED Excel.Chart.8 \s ���
































































































































































































































































































































































































































Cascades Island lamprey modifications.





AFF picket leads.












-  -
PAGE  
11

- 11 -


_1226756700.xls
Chart2

		38426		4		0		0

		38427		-22		0		0

		38428		-109		0		0

		38429		-12		0		0

		38430		11		0		0

		38431		30		0		0

		38432		7		0		0

		38433		7		0		0

		38434		12		0		0

		38435		3		0		0

		38436		4		0		0

		38437		-1		0		0

		38438		21		0		0

		38439		29		0		0

		38440		6		0		0

		38441		4		0		0

		38442		1		0		0

		38443		15		0		0

		38444		8		0		0

		38445		19		0		0

		38446		18		0		0

		38447		22		0		0

		38448		64		0		0

		38449		27		0		0

		38450		40		0		0

		38451		26		0		0

		38452		33		0		0

		38453		27		0		0

		38454		24		0		0

		38455		81		0		0

		38456		44		0		0

		38457		32		0		0

		38458		60		0		0

		38459		58		0		0

		38460		62		0		0

		38461		85		0		0

		38462		87		0		0

		38463		85		0		0

		38464		74		0		0

		38465		66		0		0

		38466		65		0		0

		38467		79		1		0

		38468		74		1		0

		38469		74		0		0

		38470		57		0		0

		38471		36		0		0

		38472		45		0		0

		38473		48		0		0

		38474		40		0		0

		38475		63		0		0

		38476		27		0		0

		38477		63		0		0

		38478		41		0		0

		38479		33		0		0

		38480		35		0		0

		38481		18		0		0

		38482		46		0		0

		38483		12		0		0

		38484		59		0		0

		38485		44		2		0

		38486		54		4		0

		38487		57		0		0

		38488		43		0		0

		38489		75		0		0

		38490		97		0		0

		38491		89		0		0

		38492		59		0		0

		38493		54		0		0

		38494		81		0		0

		38495		72		0		0

		38496		56		0		0

		38497		35		0		0

		38498		33		0		0

		38499		34		5		0

		38500		85		20		0

		38501		100		0		0

		38502		134		9		0

		38503		201		7		0

		38504		199		10		0

		38505		174		19		0

		38506		168		18		0

		38507		140		48		0

		38508		120		61		0

		38509		193		84		0

		38510		239		168		10

		38511		238		254		-10

		38512		485		367		0

		38513		253		476		0

		38514		315		529		0

		38515		338		593		0

		38516		331		1058		0

		38517		350		1354		0

		38518		468		1729		0

		38519		384		1302		1

		38520		485		1852		-1

		38521		434		1791		0

		38522		367		2112		0

		38523		473		2471		0

		38524		606		2507		0

		38525		624		3037		0

		38526		620		2858		0

		38527		536		2340		-1

		38528		569		3078		0

		38529		621		3307		0

		38530		776		3543		0

		38531		867		3136		0

		38532		897		4102		1

		38533		596		2333		0

		38534		1313		3205		0

		38535		1509		2933		0

		38536		1786		2861		0

		38537		1833		2498		0

		38538		2173		2046		0

		38539		2667		1920		0

		38540		2587		1643		0

		38541		2157		972		0

		38542		2775		860		0

		38543		2271		658		0

		38544		2251		659		0

		38545		1915		616		0

		38546		2552		653		0

		38547		2478		500		0

		38548		2922		395		0

		38549		2796		497		0

		38550		2897		397		0

		38551		3489		526		0

		38552		3772		431		0

		38553		5082		402		0

		38554		5481		278		0

		38555		5564		160		0

		38556		6879		148		0

		38557		5879		89		0

		38558		5289		89		0

		38559		5649		83		0

		38560		6596		74		0

		38561		7042		36		0

		38562		7396		34		0

		38563		6315		30		0

		38564		4942		31		0

		38565		7729		27		0

		38566		4643		8		0

		38567		7376		18		0

		38568		5020		12		0

		38569		5350		12		0

		38570		5299		6		0

		38571		5958		6		0

		38572		5882		5		0

		38573		4120		0		1

		38574		4289		2		0

		38575		3685		4		8

		38576		3386		3		6

		38577		3851		1		2

		38578		3620		1		7

		38579		4389		2		9

		38580		6095		3		22

		38581		4968		2		4

		38582		3550		2		3

		38583		2993		2		29

		38584		2309		0		21

		38585		3381		0		158

		38586		6577		0		168

		38587		5870		0		143

		38588		4355		0		188

		38589		3984		1		264

		38590		4231		1		474

		38591		3802		0		606

		38592		4045		0		458

		38593		3733		0		275

		38594		2334		0		150

		38595		1367		0		146

		38596		1625		7		858

		38597		2122		5		2208

		38598		4159		0		3438

		38599		4867		0		3626

		38600		4311		0		4300

		38601		4310		0		4445

		38602		3716		2		3083

		38603		3870		1		3826

		38604		4030		1		4309

		38605		3172		0		2653

		38606		3238		0		2699

		38607		2967		0		2334

		38608		3002		0		1687

		38609		3066		0		2348

		38610		4677		0		3953

		38611		4744		0		2976

		38612		3324		0		1532

		38613		3482		0		1335

		38614		3329		0		1486

		38615		3744		1		1359

		38616		3638		1		715

		38617		2627		1		538

		38618		2741		0		667

		38619		2440		0		541

		38620		3001		0		609

		38621		2919		1		550

		38622		3544		0		743

		38623		2634		0		433

		38624		2786		0		569

		38625		2760		0		595

		38626		2292		1		653

		38627		2191		0		688

		38628		1853		0		659

		38629		1987		0		1054

		38630		1851		0		942

		38631		1715		0		972

		38632		1830		0		1164

		38633		1598		0		863

		38634		1519		0		1155

		38635		1176		0		1090

		38636		1275		0		987

		38637		1092		0		1211

		38638		685		0		669

		38639		726		0		813

		38640		560		0		798

		38641		647		0		769

		38642		531		-1		954

		38643		502		0		596

		38644		392		0		448

		38645		278		0		376

		38646		324		0		381

		38647		244		0		302

		38648		285		0		387

		38649		237		0		177

		38650		196		0		172

		38651		178		0		145

		38652		124		0		123

		38653		123		0		99

		38654		145		0		107

		38655		196		0		124

		38656		255		0		196



Chinook

Steelhead

Sockeye

Coho

Date

Number of Fish

4

1

2

2

1

0

4

0

0

1

0

0

0

3

5

6

0

-2

2

2

7

1

15

10

18

11

12

23

57

51

108

94

398

210

470

508

964

1346

2230

1374

1828

4149

4092

3882

2577

3681

3231

2180

1850

2142

2542

6065

2471

976

670

482

376

704

1133

791

1452

1269

1106

1626

1109

443

539

754

696

993

1028

947

887

1333

1789

1452

1511

1344

1432

1181

1152

1107

1119

1238

1706

1356

1417

1750

1770

1597

2004

2044

2471

1847

1938

1365

1567

1929

1898

2464

1824

1613

1766

1809

1844

1644

1659

953

1680

1705

2209

1889

1580

1626

1459

932

950

845

702

770

948

793

899

1054

1045

1015

588

825

788

592

724

550

474

461

429

421

337

311

308

325

190

320

215

235

301

283

229

210

450

505

377

537

555

619

529

354

184

350

1054

2563

1854

1659

1737

3226

4328

3505

4865

3994

4334

4088

12563

23215

23508

18721

13812

16104

16536

23658

24712

17976

16814

11898

12402

13063

17158

13057

7265

8751

7783

7323

6408

4619

4114

3851

3834

4790

5724

3065

2527

2541

2070

2302

2111

1247

1154

791

1526

1071

1585

802

762

929

458

577

318

539

1118

492

302

292

155

140

244

309

150

225

157

148

140

128

184



Sheet1

		





Sheet1

		38426		4		0		0

		38427		-22		0		0

		38428		-109		0		0

		38429		-12		0		0

		38430		11		0		0

		38431		30		0		0

		38432		7		0		0

		38433		7		0		0

		38434		12		0		0

		38435		3		0		0

		38436		4		0		0

		38437		-1		0		0

		38438		21		0		0

		38439		29		0		0

		38440		6		0		0

		38441		4		0		0

		38442		1		0		0

		38443		15		0		0

		38444		8		0		0

		38445		19		0		0

		38446		18		0		0

		38447		22		0		0

		38448		64		0		0

		38449		27		0		0

		38450		40		0		0

		38451		26		0		0

		38452		33		0		0

		38453		27		0		0

		38454		24		0		0

		38455		81		0		0

		38456		44		0		0

		38457		32		0		0

		38458		60		0		0

		38459		58		0		0

		38460		62		0		0

		38461		85		0		0

		38462		87		0		0

		38463		85		0		0

		38464		74		0		0

		38465		66		0		0

		38466		65		0		0

		38467		79		1		0

		38468		74		1		0

		38469		74		0		0

		38470		57		0		0

		38471		36		0		0

		38472		45		0		0

		38473		48		0		0

		38474		40		0		0

		38475		63		0		0

		38476		27		0		0

		38477		63		0		0

		38478		41		0		0

		38479		33		0		0

		38480		35		0		0

		38481		18		0		0

		38482		46		0		0

		38483		12		0		0

		38484		59		0		0

		38485		44		2		0

		38486		54		4		0

		38487		57		0		0

		38488		43		0		0

		38489		75		0		0

		38490		97		0		0

		38491		89		0		0

		38492		59		0		0

		38493		54		0		0

		38494		81		0		0

		38495		72		0		0

		38496		56		0		0

		38497		35		0		0

		38498		33		0		0

		38499		34		5		0

		38500		85		20		0

		38501		100		0		0

		38502		134		9		0

		38503		201		7		0

		38504		199		10		0

		38505		174		19		0

		38506		168		18		0

		38507		140		48		0

		38508		120		61		0

		38509		193		84		0

		38510		239		168		10

		38511		238		254		-10

		38512		485		367		0

		38513		253		476		0

		38514		315		529		0

		38515		338		593		0

		38516		331		1058		0

		38517		350		1354		0

		38518		468		1729		0

		38519		384		1302		1

		38520		485		1852		-1

		38521		434		1791		0

		38522		367		2112		0

		38523		473		2471		0

		38524		606		2507		0

		38525		624		3037		0

		38526		620		2858		0

		38527		536		2340		-1

		38528		569		3078		0

		38529		621		3307		0

		38530		776		3543		0

		38531		867		3136		0

		38532		897		4102		1

		38533		596		2333		0

		38534		1313		3205		0

		38535		1509		2933		0

		38536		1786		2861		0

		38537		1833		2498		0

		38538		2173		2046		0

		38539		2667		1920		0

		38540		2587		1643		0

		38541		2157		972		0

		38542		2775		860		0

		38543		2271		658		0

		38544		2251		659		0

		38545		1915		616		0

		38546		2552		653		0

		38547		2478		500		0

		38548		2922		395		0

		38549		2796		497		0

		38550		2897		397		0

		38551		3489		526		0

		38552		3772		431		0

		38553		5082		402		0

		38554		5481		278		0

		38555		5564		160		0

		38556		6879		148		0

		38557		5879		89		0

		38558		5289		89		0

		38559		5649		83		0

		38560		6596		74		0

		38561		7042		36		0

		38562		7396		34		0

		38563		6315		30		0

		38564		4942		31		0

		38565		7729		27		0

		38566		4643		8		0

		38567		7376		18		0

		38568		5020		12		0

		38569		5350		12		0

		38570		5299		6		0

		38571		5958		6		0

		38572		5882		5		0

		38573		4120		0		1

		38574		4289		2		0

		38575		3685		4		8

		38576		3386		3		6

		38577		3851		1		2

		38578		3620		1		7

		38579		4389		2		9

		38580		6095		3		22

		38581		4968		2		4

		38582		3550		2		3

		38583		2993		2		29

		38584		2309		0		21

		38585		3381		0		158

		38586		6577		0		168

		38587		5870		0		143

		38588		4355		0		188

		38589		3984		1		264

		38590		4231		1		474

		38591		3802		0		606

		38592		4045		0		458

		38593		3733		0		275

		38594		2334		0		150

		38595		1367		0		146

		38596		1625		7		858

		38597		2122		5		2208

		38598		4159		0		3438

		38599		4867		0		3626

		38600		4311		0		4300

		38601		4310		0		4445

		38602		3716		2		3083

		38603		3870		1		3826

		38604		4030		1		4309

		38605		3172		0		2653

		38606		3238		0		2699

		38607		2967		0		2334

		38608		3002		0		1687

		38609		3066		0		2348

		38610		4677		0		3953

		38611		4744		0		2976

		38612		3324		0		1532

		38613		3482		0		1335

		38614		3329		0		1486

		38615		3744		1		1359

		38616		3638		1		715

		38617		2627		1		538

		38618		2741		0		667

		38619		2440		0		541

		38620		3001		0		609

		38621		2919		1		550

		38622		3544		0		743

		38623		2634		0		433

		38624		2786		0		569

		38625		2760		0		595

		38626		2292		1		653

		38627		2191		0		688

		38628		1853		0		659

		38629		1987		0		1054

		38630		1851		0		942

		38631		1715		0		972

		38632		1830		0		1164

		38633		1598		0		863

		38634		1519		0		1155

		38635		1176		0		1090

		38636		1275		0		987

		38637		1092		0		1211

		38638		685		0		669

		38639		726		0		813

		38640		560		0		798

		38641		647		0		769

		38642		531		-1		954

		38643		502		0		596

		38644		392		0		448

		38645		278		0		376

		38646		324		0		381

		38647		244		0		302

		38648		285		0		387

		38649		237		0		177

		38650		196		0		172

		38651		178		0		145

		38652		124		0		123

		38653		123		0		99

		38654		145		0		107

		38655		196		0		124

		38656		255		0		196



Chinook

Steelhead

Sockeye

Coho

Date

Number of Fish

4

1

2

2

1

0

4

0

0

1

0

0

0

3

5

6

0

-2

2

2

7

1

15

10

18

11

12

23

57

51

108

94

398

210

470

508

964

1346

2230

1374

1828

4149

4092

3882

2577

3681

3231

2180

1850

2142

2542

6065

2471

976

670

482

376

704

1133

791

1452

1269

1106

1626

1109

443

539

754

696

993

1028

947

887

1333

1789

1452

1511

1344

1432

1181

1152

1107

1119

1238

1706

1356

1417

1750

1770

1597

2004

2044

2471

1847

1938

1365

1567

1929

1898

2464

1824

1613

1766

1809

1844

1644

1659

953

1680

1705

2209

1889

1580

1626

1459

932

950

845

702

770

948

793

899

1054

1045

1015

588

825

788

592

724

550

474

461

429

421

337

311

308

325

190

320

215

235

301

283

229

210

450

505

377

537

555

619

529

354

184

350

1054

2563

1854

1659

1737

3226

4328

3505

4865

3994

4334

4088

12563

23215

23508

18721

13812

16104

16536

23658

24712

17976

16814

11898

12402

13063

17158

13057

7265

8751

7783

7323

6408

4619

4114

3851

3834

4790

5724

3065

2527

2541

2070

2302

2111

1247

1154

791

1526

1071

1585

802

762

929

458

577

318

539

1118

492

302

292

155

140

244

309

150

225

157

148

140

128

184



Sheet2

		





Sheet3

		






