 
CENWP-OP-B                                                                                                        6 March 2000

MEMORANDUM FOR CENWP-OP, ATTN:  Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for weeks 8 and 9 of 2000, which covers the period 20 February through 4 March.
1.  OPERATION SUMMARY.

1.1. Daily average river flow ranged from 151.1 to 204.1 kcfs.  Daily average tailwater elevation for the project ranged from 14.3’ to 17.5’ msl.  River temperature ranged from 41 to 42° F.  Spill bays 1 and 18, which supply attraction flow for the Cascades Island ladder and Bradford Island ladder respectively, remain open 4”.  

1.2.  Unit Outages.

DATE
UNIT (S)
TIME
REASON

2/21
3, 4, 5
0654-1654
Surface collector dives

2/22
3, 4, 5, 6
~0654-1700
Surface collector dives

2/23
9
0506-1900
Dive, bus 9/10 work

2/23
2, 3, 4
0700-1734
Surface collector dives

2/24
2, 3, 4
0648-1530
Surface collector dives

2/25
5
1018-1312
STS installation

2/28
8
0707-1606
ESBS installation

2/28
11, 12, 13, 14
~2 hours each
Dive, trashrack transducer installation

2/29
8
0642-0842
Complete ESBS installation

2/29
15, 16, 17
~2 hours each
Dive, trashrack transducer installation

2/29
2
0800-1712
Instrumentation installation

3/1
16, 17
0706-1624
Dive, trashrack transducer installation

3/1
6
0836
Remove turbine release pipes and equip.

3/2
1, 2
~4 hours each
STS installation

3/2
13, 14, 15
1100-1736
Dive, trashrack transducer installation

3/3
11, 12, 13, 16, 17
~2 hours each
STS installation

3/4
14, 15
~3 hours each
STS installation

1.3.  The first powerhouse ice and trash sluiceway remained open according to surface collector dive locations.  The second powerhouse sluiceway remained closed with one exception.  The sluiceway was opened from 0804-0912 on 3 March for debris removal.  
1.4.  Second powerhouse fish units remained in service.  The units are being placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.
2.  ACTIVITIES. 
2.1.  Fish Ladder and DSM Service.  The Bradford Island B-branch ladder and PH1 DSM returned to service on 25 and 28 February, respectively.  

2.2. AWS Closures.  FV4-3 was closed for cleaning from 1352-1422 on 4 March, and the Bradford Island exit was partially closed for cleaning from 1500-1512 on 4 March.   

2.3. Dewaterings and Fish Salvage.  Unit 6 was dewatered on 1 March to remove turbine release pipes.  Project biologists recovered 4 juvenile salmonids from the scroll case.  All fish were released in good condition.       

3.  RESEARCH. 
3.1. PH2 Bypass System Evaluation.  NMFS began releasing dye-marked fry into the PH2 DSM on 1 March to determine if fish condition is adversely affected by system passage and to confirm that fry are retained within the system.    

3.2. WDFW Fish Counting.  WDFW continued 24-h/d video counting at Bradford Island and Washington shore. 

4.  FISHWAYS.  Project biologists inspected on 22 and 25 February and 1 and 3 March these reporting weeks.

4.1. Fish Passage Plan Observations. 

DATE
LOCATion
FPP Deviation
CAUSE
RESPONSE

Both Weeks.

Project biologists only completed 4 of the required 6 inspections these reporting weeks. 
Short staffed and additional activities.
Operators continue to inspect fishways daily.

Both Weeks.
PH1 collection channel velocity meter.
Meter was not working and should register 1.5-4.0 fps.
Unknown.
No action taken.

Both Weeks.
PH2 collection channel velocity meter.
Meter was not working and should register 1.5-4.0 fps.
Unknown.
No action taken.

2/22, 2/25
A-branch ladder staff gauge.
Staff gauge registered .8’ over the weir and should register 1.0’+/-. 1’.
FV3-9 was closed to preclude water from overtopping weir blocks down B-branch.  Consequently, water levels fluctuate down A-branch depending on forebay elevation.
No action taken.  FV3-9 was opened and adjusted accordingly when B-branch returned to service on 25 February.

2/25, 3/1, 3/3
PH2 entrance gates NDE and SUE.
Gates registered <13’ of submergence.
Gates have been in manual control due to raise/lower limit switch problems.
Gates are awaiting repair and are being operated in manual control.

3/1, 3/3
PH1 chain gate 10C.
Gate was not fully open per the FPP.
Chain gate was closed to remove a log and was not reopened. 
Gate was adjusted on 7 March.

4.2. Fish Ladder Temperatures.  Readings are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder below the count station at Washington shore.  Temperatures are supplied by The Fisheries Field Unit.
Date
Wash. Shore
Bradford Is.

3/3
5.1
5.0

3/4
5.2
5.1

                                                 Fish Ladder Temperatures ((C) 
4.3. Sensor Calibration.  Water level sensors were checked for calibration on 23 February and 1 March these reporting weeks.   

4.4. Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

                                                                                                     DEBORAH L. CHENOWETH

                                 

                                                              Operations Project Manager

3
2

