 
CENWP-OP-B                                                                                                      14 March 2000

MEMORANDUM FOR CENWP-OP, ATTN:  Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 10 of 2000, which covers the period 5 through 11 March.
1.  OPERATION SUMMARY.

1.1. Daily average river flow ranged from 164.4 to 214.5 kcfs.  Daily average tailwater elevation for the project ranged from 15.4’ to 18.1’ msl.  Daily average spill ranged from 16.5 to 113.8 Kcfs on 9 through 11 March this reporting week for the Spring Creek release.  River temperature ranged from 42 to 43° F.  Spill bays 1 and 18, which supply attraction flow for the Cascades Island ladder and Bradford Island ladder respectively, remain open 4”.  

1.2.  First powerhouse unit 10 remained out of service for stator rewind.  Unit 5 was taken out of service at 2000 on 9 March in preparation for turbine release pipe removal.  Unit 6 returned to service following turbine release pipe removal at 1500 on 10 March.  

1.3.  The first powerhouse ice and trash sluiceway remained open this reporting week.  The second powerhouse sluiceway was opened to elevation 68’ at 1953 on 9 March in accordance with the special operation for the Spring Creek release.
1.4.  Second powerhouse fish units remained in service with the following exception.  Fish unit 2 was out of service from 0300-0706 on 7 March due to a field breaker failure.  The units are being placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.
2.  ACTIVITIES. 
2.1. AWS Closures.  FV1-1 was closed for cleaning at 1620 on 6 March.  Following cleaning, the valve would not open and maintenance crews found that the motor was burned-up.  Crews worked overtime and completed replacing the motor on the following morning.  The valve was placed back in automatic control at 0844 on 7 March.  To maintain collection channel differentials, orifice gate 62 was closed.  The collection channel remained in criteria during the outage.  FV5-9 was closed for cleaning from 1600-1621 on 10 March.   

2.2. Dewaterings and Fish Salvage.  There was no dewaterings or fish salvage this reporting week.
3.  RESEARCH. 
3.1. PH2 Bypass System Evaluation.  NMFS continued releasing chinook fry into the PH2 DSM to determine if fish condition is adversely affected by system passage.  They also began PIT tagging juvenile chinook for release through the new bypass system as part of their post construction evaluation. 

3.2. PSMFC Smolt Monitoring.  NMFS began 24-h/d PIT tag interrogation at PH2 JMF on 7 March. 

3.3. WDFW Fish Counting.  WDFW continued 24-h/d video counting at Bradford Island and Washington shore. 

4.  FISHWAYS.  Project biologists inspected on 6, 7, 9, and 10 March this reporting week.

4.1. Fish Passage Plan Observations. 

DATE
LOCATion
FPP Deviation
CAUSE
RESPONSE

3/6, 3/7, 3/9
PH1 collection channel velocity meter.
Meter was not working and should register 1.5-4.0 fps.
Broken cable.
Meter was repaired on 9 March.

3/6, 3/7
PH2 collection channel velocity meter.
Meter was not working and should register 1.5-4.0 fps.
Unknown.
Meter was inspected on 9 March.

4.2. Fish Ladder Temperatures.  Readings are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder below the count station at Washington shore.  Temperatures are supplied by The Fisheries Field Unit.
Date
Wash. Shore
Bradford Is.

3/5
5.3
5.2

3/6
5.3
5.2

3/7
5.4
5.3

3/8
5.5
5.4

3/9
5.6
5.5

3/10
5.8
5.8

3/11
5.9
5.8

                                                 Fish Ladder Temperatures ((C) 
4.3. Sensor Calibration.  Water level sensors were checked for calibration on 9 March this reporting week.   

4.4. Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

5.  OTHER.

5.1. Special Operation for Spring Creek Hatchery Release.  The special operation for the Spring Creek hatchery release was initiated at 2000 on 9 March.  The operation called for 100 Kcfs spill at total flow of 200-220 Kcfs and 80 Kcfs spill at total flow of 180-200 Kcfs.  The PH2 ice and trash sluiceway was opened to elevation 68’.

                                                                                                     DEBORAH L. CHENOWETH

                                 

                                                              Operations Project Manager

//S//

2
3

