 
CENWP-OP-B                                                                                                     01 August 2000

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 30 of 2000, which covers the period 23 July through 29 July.
1.  OPERATION SUMMARY.

1.1 Average daily river flow ranged from 148.1 to 181.3 kcfs.  Daily average spill ranged from 81.3 to 98.8 kcfs.  Average daily tailwater elevation for the project ranged from 13.1’ to 15.5’ msl.  Average daily forebay elevation for the project ranged from 73.8’ to 74.1’ msl.  River temperature ranged from 68 to 70° F.  Spill bays 1 and 18, which supply attraction flow for Cascades Island ladder and Bradford Island ladder respectively, remain open 4”.

1.2 Unit 12 remained out of service for stator rewedge and 4-year overhaul.  Unit 3 went out of service 0748 23 July for turbine rehab. 
1.3 The first powerhouse ice and trash sluiceway remained open this reporting week.  PH1 chain gates are being operated according to PSC testing requirements.     
1.4 Second powerhouse fish units are in service and operating normally this week.  The units are being placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.
2.  ACTIVITIES. 
2.1 AWS Closures.  FV3-6 closed 1545-1600 27 July for cleaning.

2.2 Dewatering and Fish Salvage.  Unit 3 draft tube- recovered 1 live sturgeon, 1 dead sturgeon, and 6 live lamprey.

2.3 STS Inspections.  No STS’s were inspected this reporting week.  

3.   RESEARCH. 
3.1. AFC&MF Adult PIT-tag Interrogation.  The 18” orifice inserts remain installed in the return ladder of the AFC&MF.  NMFS will resume testing and PIT-tagging adults from the lab to get estimates of reading efficiencies for the 18” and 26” orifice inserts following shad passage season.

3.2. AFC&MF Adult Sampling and Tagging.  The University of Idaho continued radio tagging and tracking adult chinook for their adult telemetry research.  They are currently sampling 7 days per week.  CRITFC and ODFW are sampling adult chinook and steelhead approximately 2 days per week for their age composition research.  

3.3. Fisheries Field Unit Video Monitoring.  The Fisheries Field Unit is assisting NMFS adult PIT-tag interrogation work this year during their testing at the AFC&MF.  They are monitoring submerged orifice and overflow weir passage in the return ladder of the AFC&MF and assisting NMFS in verifying passage of streamer-marked PIT-tag fish during their testing.  They are also periodically monitoring submerged orifice and overflow weir passage at Cascades Island and Washington Shore ladders this year.

3.4. Normandeau/Mid-Columbia Consulting/Battelle PH2 Sluicechute Survival Testing.  Researchers will resume releasing balloon tagged fish through the second powerhouse ice and trash sluiceway for survival testing in mid September.  This work is in support of corner collector research.  

3.6. NMFS Lamprey Tagging and Radio Tracking.  NMFS continued trapping and tagging lamprey in the AFC&MF.  They are releasing the radio tagged fish downstream and tracking the fish back through the project in cooperation with the University of Idaho.

3.7. PH2 Bypass System Evaluation. USGS completed their releases of radio-tagged juveniles this reporting week.  They had been releasing fish in the DSM and tracking from the outfall to Beacon Rock. 

3.8. PSMFC DSM1 and JMF Smolt Monitoring.  PSMFC continued 24-h/d PIT tag interrogation at DSM1 and PH2 JMF.  They are sampling daily from 1600-2400 at DSM1 and approximately 0800-1000 at PH2 JMF.

3.9. University of Idaho Lamprey Test Flume.  The University of Idaho continued testing lamprey-swimming capabilities under various flow conditions in the lamprey test flume at the AFC&MF this reporting week.  Testing will continue through early August depending on lamprey availability.    

3.10. USGS Radio-Tracking.  USGS completed releasing and radio-tracking juveniles this reporting week.  They were tracking juveniles as part of the PH1 surface collector monitoring.

3.11. WDFW Fish Counting.  WDFW continued 16-h/d visual and 8-h/d video counting at Bradford Island and Washington shore. 

3.12. WES/Battelle Hydroacoustic Monitoring.  WES and Battelle completed hydroacoustic monitoring of the PH1 surface collector this reporting week.

4.  FISHWAYS.  Project biologists inspected on 25, 26 and 28 July this reporting week.

4.1 

Fish Passage Plan Observations.

DATE
LOCATion
FPP Deviation
CAUSE
RESPONSE

All week
Cascades Island diffuser FG6-18.
Diffuser is stuck partially open and should be closed.
Unknown.
Will repair during winter maintenance period.

All week.
PH1 and PH2 collection channel electronic velocity meter.
Meter was not working and should register 1.5-4.0 fps per the FPP.
Unknown.
Investigating alternative method of measure.  



4.2  Fish Ladder Temperatures.  Readings are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures supplied by Fisheries Field Unit.
Date
Wash. Shore
Bradford Is.

7/23
20.1
20.0

7/24
20.3
20.2

7/25
20.4
20.3

7/26
20.4
20.3

7/27
20.6
20.4

7/28
20.7
20.6

7/29
21.0
20.9

                                                 Fish Ladder Temperatures ((C) 
4.3 Sensor Calibration.  Water level sensors were checked for calibration on 27 July this reporting week.  Electricians notified south channel sensors are out of calibration.

4.4 Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

5. MISCELLANEOUS

5.1 FV1-1 in manual most of the week due to PH1 collection channel not controlling properly.

5.2 Bradford Island operated in manual 1555 25 July until 1045 26 July due to severed wires.

5.3 Cascade Island computer down 0930 29 July.  FV5-3, 5-4 in manual.

5.4 Monitoring facility switched over to low outfall 1415 26 July, when tailwater elevations stabilized around 13.5’.  The switchgate will be operated in manual until the leakage under the gate is reduced to a point where head isn’t required in the unused outfall flume.

                                                                                                     DEBORAH L. CHENOWETH

                                 

                                                              Operations Project Manager

//S//

2
2

