 
CENWP-OP-B                                                                                                     21 August 2000

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 33 of 2000, which covers the period 13 August through 19 August.
1.  OPERATION SUMMARY.

1.1 Average daily river flow ranged from 144.8 to 175.9 kcfs.  Average daily spill ranged from 84.9 to 113.7 kcfs.  Average daily tailwater elevation for the project ranged from 12.9’ to 15.2’ msl.  Average daily forebay elevation for the project ranged from 73.2’ to 73.5’ msl.  River temperature ranged from 69 to 71° F.  Spill bays 1 and 18, which supply attraction flow for Cascades Island ladder and Bradford Island ladder respectively, remain open 4”.

1.2 Unit 12 remained out of service for stator rewedge and 4-year overhaul.  Unit 3 remained out of service for turbine rehab.  Unit 4 remained out of service for its 100 day inspection.  Unit 6 remained out of service for index testing.  Unit 5 went out of service from 0600 until 1712 14 August, 0600 until 1612 15 August for PSC dives and from 1248 until 1354 18 August for transducer removal.  Unit 2 went out of service from 0600 until 1524 16 August, 0500 until 1612 17 August, 0530 until 1212 18 August for PSC dives and from 1400 until 1512 18 August for transducer removal.  Unit 1 went out of service from 0706 until 1624 17 August and 0530 until 1206 18 August for PSC dives.  Unit 7 went out of service from 0530 until 0700 18 August due to a high STS amp reading.
1.3 The first powerhouse ice and trash sluiceway was open 
1.4 Second fish units were operated normally all week.  The units are being placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.
2.  ACTIVITIES. 
2.1 AWS Closures.  FV3-9 closed from 1530 until 1545 18 August for cleaning.

2.2 Dewatering and Fish Salvage.  No salvaging this week.

2.3 STS Inspections.  Seven STSs were inspected this reporting week.  

Unit
Date
Run Hours
Comments

11
8/14
77
Video taped gaps around VBS

1
8/17
910


5
8/17
697


7
8/17
713


8
8/17
1924
ESBS

9
8/17
625


10
8/17
895


3.   RESEARCH. 
3.1 AFC&MF Adult PIT-tag Interrogation.  The 18” orifice inserts remain installed in the return ladder of the AFC&MF.  NMFS will resume testing and PIT-tagging adults from the lab to get estimates of reading efficiencies for the 18” and 26” orifice inserts following shad passage season.

3.2 AFC&MF Adult Sampling and Tagging.  The University of Idaho continued radio tagging and tracking adult chinook for their adult telemetry research.  They are currently sampling 7 days per week.  CRITFC and ODFW are sampling adult chinook and steelhead approximately 2 days per week for their age composition research.  

3.3 Fisheries Field Unit Video Monitoring.  The Fisheries Field Unit is assisting NMFS adult PIT-tag interrogation work this year during their testing at the AFC&MF.  They are monitoring submerged orifice and overflow weir passage in the return ladder of the AFC&MF and assisting NMFS in verifying passage of streamer-marked PIT-tag fish during their testing.  They are also periodically monitoring submerged orifice and overflow weir passage at Cascades Island and Washington Shore ladders this year.

3.4 Normandeau/Mid-Columbia Consulting/Battelle PH2 Sluicechute Survival Testing.  Researchers will resume releasing balloon tagged fish through the second powerhouse ice and trash sluiceway for survival testing in mid September.  This work is in support of corner collector research.  

3.5 NMFS Lamprey Tagging and Radio Tracking.  NMFS continued trapping and tagging lamprey in the AFC&MF.  They are releasing the radio tagged fish downstream and tracking the fish back through the project in cooperation with the University of Idaho.

3.6 PSMFC DSM1 and JMF Smolt Monitoring.  PSMFC continued 24-h/d PIT tag interrogation at DSM1 and PH2 JMF.  They are sampling daily from 1600-2400 at DSM1 and approximately 0800-1000 at PH2 JMF.

3.7 University of Idaho Lamprey Test Flume.  The University of Idaho continued testing lamprey-swimming capabilities under various flow conditions in the lamprey test flume at the AFC&MF this reporting week.  Testing will continue through early August depending on lamprey availability.    

3.8 WDFW Fish Counting.  WDFW continued 16-h/d visual and 8-h/d video counting at Bradford Island and Washington shore.   

3.9 WDFW/ODFW Fall Chinook counting.  WDFW and ODFW started counting Fall Chinook at the Bradford Island and Washington shore count stations during the day.

3.10 Yakima Nation.  Tribal members are fishing for northern pikeminnow from the powerhouses during the afternoon and evening hours.

4.  FISHWAYS. 
4.1 Project biologists inspected on 14, 16 and 17 August this reporting week.  NMFS inspected 14 August.

4.2 Fish Passage Plan Observations.

DATE
LOCATion
FPP Deviation
CAUSE
RESPONSE

All week
Cascades Island diffuser FG6-18.
Diffuser is stuck partially open and should be closed.
Unknown.
Will repair during winter maintenance period.

All week.
PH1 and PH2 collection channel electronic velocity meter.
Meter was not working and should register 1.5-4.0 fps per the FPP.
Unknown.
Investigating alternative method of measure.  



4.2 Fish Ladder Temperatures.  Readings are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are supplied by Fisheries Field Unit.
Date
Wash. Shore
Bradford Is.

8/13
21.0
20.9

8/14
20.8
20.6

8/15
20.7
20.5

8/16
20.6
20.4

8/17
20.5
20.4

8/18
20.4
20.2

8/19
20.3
20.2

                                                 Fish Ladder Temperatures ((C) 
4.3 Sensor Calibration.  Water level sensors were checked for calibration on 16 August this reporting week.  

4.4 Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

5. Miscellaneous

5.1 The Monitoring Facility was put back into sample mode at 1805 13 August.

                                                                                                     DEBORAH L. CHENOWETH

                                 

                                                              Operations Project Manager

//S//

2
3

