 
CENWP-OP-B                                                                                               11 September 2000

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 36 of 2000, which covers the period 03 September through 09 September.
1.  OPERATION SUMMARY.

1.1 Average daily river flow ranged from 93.6 to 139.7 kcfs.  Spill has been stopped.  Average daily tailwater elevation for the project ranged from 9.1’ to 12.1’ msl.  Average daily forebay elevation for the project ranged from 73.8’ to 74.5’ msl.  River temperature ranged from 67 to 68° F.  Spill bays 1 and 18, which supply attraction flow for Cascades Island ladder and Bradford Island ladder respectively, remain open 4”.

1.2 Unit 12 remained out of service for stator re-wedge and 4-year overhaul.  Unit 3 remained out of service for turbine rehab.  Unit 4 returned to service 1212 7 September from its 100 day inspection, then went out of service again 1624 8 September due to high bearing temperatures.  Unit 6 remained out of service for 100-day inspection.  Unit 1 went out of service from 0406 5 September until 1442 7 September for semi annual electrical maintenance.  Unit 15 went out of service from 0706 until 0930 6 September for STS repair.  Unit 16 went out of service from 0948 until 1524 6 September for STS removal.  Unit 13 went out of service from 1836 6 September until 1330 7 September due to an oil tube leak.
1.3 Second fish units were operated normally all week.  The units are being placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.
2.  ACTIVITIES. 
2.1 AWS Closures.  FV3-9 was closed for cleaning from 1556 until 1610 7 September.  FV3-9 was closed for emergency dewatering of Bradford Island from 1340 until 1516 8 September.

2.2 Dewatering and Fish Salvage. On 5 September biologists recovered 12 live sturgeon, 20 dead sturgeon, and one channel catfish from Unit 4 draft tube.  On 6 September biologists recovered 2 sculpin from Unit 4 tail logs.

2.3 STS Inspections.  No STSs were inspected this reporting week.  

3.   RESEARCH. 
3.1 AFC&MF Adult PIT-tag Interrogation.  The 18” orifice inserts remain installed in the return ladder of the AFC&MF.  NMFS will resume testing and PIT-tagging adults from the lab to get estimates of reading efficiencies for the 18” and 26” orifice inserts 13 September through 28 September.

3.2 AFC&MF Adult Sampling and Tagging.  The University of Idaho continued radio tagging and tracking adult Chinook for their adult telemetry research.  They are currently sampling 7 days per week.  CRITFC and ODFW are sampling adult Chinook and steelhead approximately 2 days per week for their age composition research.  

3.3 Fisheries Field Unit Video Monitoring.  The Fisheries Field Unit is assisting NMFS adult PIT-tag interrogation work this year during their testing at the AFC&MF.  They are monitoring submerged orifice and overflow weir passage in the return ladder of the AFC&MF and assisting NMFS in verifying passage of streamer-marked PIT-tag fish during their testing.  They are also periodically monitoring submerged orifice and overflow weir passage at Cascades Island and Washington Shore ladders this year.

3.4 Normandeau/Mid-Columbia Consulting/Battelle PH2 Sluicechute Survival Testing.  Researchers will resume releasing balloon tagged fish through the second powerhouse ice and trash sluiceway for survival testing in mid September.  This work is in support of corner collector research.  

3.5 NMFS Lamprey Tagging and Radio Tracking.  NMFS continued trapping and tagging lamprey in the AFC&MF.  They are releasing the radio tagged fish downstream and tracking the fish back through the project in cooperation with the University of Idaho.

3.6 PSMFC DSM1 and JMF Smolt Monitoring.  PSMFC finished 24-h/d PIT tag interrogation at DSM1 as of 0012 9 September.  They continued PIT tag interrogation and 24 h/d sampling at PH2 JMF.

3.7 University of Idaho Lamprey Test Flume.  The University of Idaho continued testing lamprey-swimming capabilities under various flow conditions in the lamprey test flume at the AFC&MF this reporting week.     

3.8 WDFW Fish Counting.  WDFW continued 16-h/d visual and 8-h/d video counting at Bradford Island and Washington shore.   

3.9 WDFW/ODFW Fall Chinook counting.  WDFW and ODFW started counting Fall Chinook at the Bradford Island and Washington shore count stations during the day.

3.10 Yakima Nation.  Tribal members are fishing for northern pikeminnow from the powerhouses during the afternoon and evening hours.

4.  FISHWAYS. 
4.1 Project biologists inspected on 05, 06, 07, and 08 September this reporting week.  

4.2 Fish Passage Plan Observations.

DATE
LOCATion
FPP Deviation
CAUSE
RESPONSE

All week
Cascades Island diffuser FG6-18.
Diffuser is stuck partially open and should be closed.
Unknown.
Will repair during winter maintenance period.

All week.
PH1 collection channel electronic velocity meter.
Meter was not working and should register 1.5-4.0 fps per the FPP.
Unknown.
Investigating alternative method of measure.  



9/5-9/7
PH2 collection channel electronic velocity meter.
Meter was not working and should register 1.5-4.0 fps per the FPP.
Works intermittently
Investigating alternative method of measure.  



9/8
Cascade Island entrance gates.
Both gates were open, only the North gate should have been.
Computer and Monitor having some problems.
Operators closed South gate.

4.2 Fish Ladder Temperatures.  Readings are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are supplied by Fisheries Field Unit.
Date
Wash. Shore
Bradford Is.

9/3
19.6
19.5

9/4
19.6
19.5

9/5
19.3
19.2

9/6
19.1
19.0

9/7
19.2
19.1

9/8
19.2
19.0

9/9
19.0
18.9

                                                 Fish Ladder Temperatures ((C) 
4.3 Sensor Calibration.  Water level sensors were checked for calibration on 06 September this reporting week.  

4.4 Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

5. MISCELLANEOUS

5.1 Bradford Island fishway was shut down from 1340 until 1500 08 September to remove salmon and steelhead from add-in portion of the ladder.

                                                                                                     DEBORAH L. CHENOWETH

                                 

                                                              Operations Project Manager

//S//

1
3

