 
CENWP-OP-B                                                                                               04 December, 2000

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 48 of 2000, which covers the period 26 November through 02 December.
1.  OPERATION SUMMARY.

1.1 Average daily river flow ranged from 130.3 to 132.9 kcfs.  Average daily tailwater elevation for the project ranged from 11.7’ to 12.5’ msl.  Average daily forebay elevation for the project ranged from 72.0’ to 74.6’ msl.  River temperature ranged between 46 and 48° F.  Spill bays 1 and 18, which supply attraction flow for Cascades Island ladder and Bradford Island ladder respectively, remain open 4”.

1.2 Unit 2 remained out of service for it’s four-year overhaul.  Unit 3 remained out of service for turbine rehab.  Unit 13 returned to service at 1948 27 November.  Unit 4 went out of service from 1006 27 November until 1548 02 December for bank ¾ lowside brushing replacement.  Unit 13 went out of service at 1948 02 December due to oil overheating.
1.3 Second powerhouse fish units operated normally this reporting week.  The units are being placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.
2.  ACTIVITIES. 
2.1 AWS Closures.  FV1-1 was closed for cleaning from 1500 until 1515 on 29 November.  FV3-9 closed for cleaning from 1530 until 1545 on 29 November.  

2.2 Dewatering and Fish Salvage.  15 Sculpin and 1 Sturgeon were recovered from Unit 2 tail logs on 01 December.

2.3 STS Inspections.  Seven STS’s were video inspected this reporting week.

UNIT
DATE
RUN HOURS
COMMENTS

11
12/04
740
C slot had six 6” rips.

12
11/28
741


14
11/28
692


15
11/28
683


16
11/29
693


17
11/29
740


18
11/29
693


3.   RESEARCH. 
3.1 AFC&MF Adult PIT-tag Interrogation.  The 26” orifice inserts and shields remain installed in the return ladder of the AFC&MF.  

3.2 AFC&MF Adult Sampling and Tagging. WDFW is sampling adult steelhead approximately 7 days per week, throughout the winter, for age composition research.  

3.3 Fisheries Field Unit Video Monitoring.  The Fisheries Field Unit is assisting NMFS adult PIT-tag interrogation work this year during their testing at the AFC&MF.  They are monitoring submerged orifice and overflow weir passage in the return ladder of the AFC&MF and assisting NMFS in verifying passage of streamer-marked PIT-tag fish during their testing.  They are also periodically monitoring submerged orifice and overflow weir passage at Cascades Island and Washington Shore ladders this year.

3.4 NMFS Lamprey Tagging and Radio Tracking.  NMFS completed trapping and tagging lamprey in the AFC&MF.  They are still tracking the fish back through the project in cooperation with the University of Idaho.

3.5 WDFW Fish Counting.  WDFW continues 24-h/d video counting at Bradford Island and Washington shore.   

4.  FISHWAYS. 
4.1 Project biologists inspected on 27, 28, 29, 30 November, and 01 December this reporting week.

4.2 Fish Passage Plan Observations.

DATE
LOCATion
FPP Deviation
CAUSE
RESPONSE

All week
Cascades Island diffuser FG6-18.
Diffuser is stuck partially open and should be closed.
Unknown.
Will repair during winter maintenance period.

All week.
PH1 and PH2 collection channel electronic velocity meter.
Meter was not working and should register 1.5-4.0 fps per the FPP.
Unknown.
Investigating alternative method of measure.  



All week
Cascade Island bird wires.
One wire is down.
Rangers cut wire to remove entangled gull.
Will repair during winter maintenance period.

All week
FG3-3, FG3-4
FG3-3 fails to fully open.
Mechanical trouble.
Will repair during winter maintenance.  FG3-4 is open to supplement FG3-3.

12/1
Bradford Island FG3-25.
Diffuser valve OOS.
Mechanical.
Will be repaired during winter maintenance season.

11/27
Bradford Island, A and B branch staff gauges
Water levels are less than 1’ (+/- .1’) over the weirs.
FV3-9 failure.
FV3-9 manually operated when forebay changes.  Will repair during winter maintenance

4.3 Fish Ladder Temperatures.  Readings are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are supplied by Fisheries Field Unit.

Date
Wash. Shore
Bradford Is.

11/26
8.1
8.0

11/27
8.1
8.1

11/28
7.9
7.8

11/29
7.5
7.4

11/30
7.6
7.4

12/01
7.5
7.4

12/02
7.3
7.2

                                                 Fish Ladder Temperatures ((C) 
4.3 Sensor Calibration.  Water level sensors were checked for calibration on 29 November this reporting week.  

4.4 Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

5. MISCELLANEOUS

5.1 Because of mechanical reasons, DSM2 screen cleaners are run once per shift (or more often depending on debris loads) to reduce wear and tear on the equipment. 

5.2 Due to unknown problems, FV3-9 will control automatically as the forebay rises, but as the water level drops an operator has to manually adjust the valve.  Valve is left in auto for now.   The problem will be addressed during Bradford Island ladder’s maintenance outage beginning 5 December.

                                                                                                     DEBORAH L. CHENOWETH

                                 

                                                              Operations Project Manager

//S//

2
3

