 
CENWP-OP-B                                                                                               22 January, 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 03 of 2001, which covers the period 14 through 20 January.
1.  OPERATION SUMMARY.

1.1 Average daily river flow ranged from 128.8 to 158.0 kcfs.  Average daily tailwater elevation for the project ranged from 11.7’ to 13.6’ msl.  Average daily forebay elevation for the project ranged from 74.7’ to 76.3’ msl.  River temperature averaged between 44 and 45° F.  Spill bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, remained open 4”.

1.2 Unit 3 remained out of service for turbine rehab.   On 17 January the following units were out of service for trash raking; Unit 14 from 0800 until 0900, Unit 15 from 0900 until 1024, Unit 16 from 1024 until 1112, Unit 17 from 1112 until 1124, Unit 18 from 1124 until 1218 and Unit 11 from 1218 until 1424.

1.3 Fish Units 1 and 2 remain out of service for annual maintenance. 

2.  ACTIVITIES. 
2.1 AWS Closures.  FV6-9 remains out of service while the Washington Shore ladder is dewatered.  

2.2 STS Inspections.  STS’s are pulled from all units.

2.3 Dewatering and Fish Salvage.   No fish salvage this reporting week.

 
3.   RESEARCH. 

3.1 NMFS Lamprey Tagging and Radio Tracking.  NMFS completed trapping and tagging lamprey in the AFC&MF.  They are still tracking the fish back through the project in cooperation with the University of Idaho.

3.2 WDFW Fish Counting.  WDFW continues 24-h/d video counting at Cascade Island and Bradford Island.

4.  FISHWAYS. 
4.1 Project biologists inspected on 16, 17, and 18 January this reporting week.

4.2 Fish Passage Plan Observations.

DATE
LOCATion
FPP Deviation
CAUSE
RESPONSE

All week
Cascades Island diffuser FG6-18.
Diffuser is stuck partially open and should be closed.
Unknown.
Will repair during winter maintenance period.

All week.
PH1 collection channel electronic velocity meter.
Meter was not working and should register 1.5-4.0 fps per the FPP.
Unknown.
Investigating alternative method of measure.  

All week
Cascade Island bird wires.
One wire is down.
Rangers cut wire to remove entangled gull.
Will repair during winter maintenance period.

All week
Chain Gate 7A
Gate was closed.  Should be set to 72’ msl.
Riggers are unable to remove the bulkhead in the slot.
Waiting for the proper equipment to remove bulkhead.

4.3  Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Thermometers are currently undergoing calibration.
4.4 Sensor Calibration.  Water level sensors were checked for calibration on 17 January this reporting week. 

4.5 Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

5. MISCELLANEOUS

5.1 Because of mechanical reasons, DSM2 screen cleaners are run once per shift (or more often depending on debris loads) to reduce wear and tear on the equipment. 

5.2 Cascades Island exit remains open to allow fish passage while Washington shore is out of service.  
5.3 DSM1 remains out of service for maintenance.
                                                                                                     DEBORAH L. CHENOWETH

                                 

                                                              Operations Project Manager

//S//

1
2

