 
CENWP-OP-B                                                                                                                                  30 July 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 30 of 2001, which covers the period 22 through 28 July.
1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 78.4 to 96.7kcfs.  Daily spill averaged 0.0 to 9.8kcfs.  Daily project tailwater elevation averaged 8.5’ to 9.3’ msl.  Daily project forebay elevation averaged 75.0’ to 75.7’ msl.  River temperature averaged 65 to 68° F.  

1.2 Spill bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, remain open 4”.  Night spill (2000 until 0100) of 45 kcfs began on 24 July and will continue until further notice.

1.3 Unit 3 remains out of service for turbine rehab.  Unit 17 remains out of service for its four-year overhaul.  Unit 5 remains out of service for turbine rehab.  Units 6, 7, and 8 returned to service at 1224 on 26 July.  Unit 7 went out of service at 2200 on 28 July due to STS problems.    

1.4 Second Powerhouse fish units remain in service.  They provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  

2.  ACTIVITIES. 
2.1 AWS Closures. FV4-3 and FV4-4 at B-branch and FV5-3 and FV5-4 are all operating in manual until the new computer system is calibrated.  

2.2 STS/VBS Inspections.  Two STSs were video inspected this reporting week.

Unit
Date
Run Hours
Comments

11
7/25
653


18
7/25
653


Table 1.  STS/VBS Inspection Data.

2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage this reporting week.

3.  RESEARCH.

3.1 WDFW Fish Counting.  WDFW continues 16-hour visual counts and 8-hour video counts at Bradford Island and Washington Shore ladders.

3.2 NMFS Saltwater rearing. The Saltwater rearing facility is in operation.  Sampling May- November.

3.3 PSMFC Adult PIT.  Looking at A and B branch and Cascade Island for noise interference.  Analyzing data collected at the Washington Shore ladder.

3.4 PSMFC Smolt Monitoring Program.  Collection continues 24h/d at the monitoring facility.  24 h/d flat plate monitoring at DSM1.

3.5 WES Hydroacoustic Monitoring.  Equipment removal scheduled 30 July – 9 August.

3.6 UI Barging Condition and Separation By Code study.  Fall Chinook separation by code study runs 15 July through 17 September. 

3.7 USGS Juvenile Radiotracking.  Equipment removal in progress.

3.8 UI Adult Fallback. UI Adult Radiotracking/Tagging.  PCC entrance gates at Powerhouse One are being operated according to UI request until 31 October.  Tagging of Chinook began at the AFC&MF 2 April and will continue seven days a week until the end of September. 

3.9 CRITFC/ODFW/WDFW Adult Trapping/Tagging.  Tagging Spring Chinook and steelhead on Tuesdays and Thursdays.

3.10 NMFS Lamprey.  Lamprey are tagged and tracked throughout the week.  Spillway ladder entrances manually operated at night for a .5’ differential.  NMFS is collecting fish for USGS.

3.11 YIN Northern Pikeminnow Dam Angling.  Fishing 25 June – 30 September.

4.  FISHWAYS. 
4.1 Project biologists inspected 22-25 and 27-28 July this reporting week.  

4.2 Fish Passage Plan Observations.

DATE
LOCATion
FPP Deviation
CAUSE
RESPONSE
TR/WAR

All week
PH2 collection channel electronic velocity meter.
PH2 is not yet working.
Not fully installed.
New velocity meter installed in channel, awaiting core drilling at PH2.  


All week
FG3-28
Out of service
Manually closed because of displaced diffuser valve cover.
New covers are being designed, and will be installed during winter maintenance.
20013904

All week
FG3-27
Not in correct position for TW elevation.
FG3-27 is open to replace FG3-28.
No action taken.


7/22, 7/23, 7/25
PH1 Collection channel velocity
Velocity meter registers less than 1.5 fps.
Water backs up in the channel during OG/SG tests.  
Monitoring situation.


All week
Main Dam Avian wires
Wires removed.
Spillway deflector installation.
Wire grid to be replaced in Mid-April when work is done.


7/25
Entrance gates at Cascade Island Ladders.
Not in correct position for TW elevation.
Computer system not yet functioning. Ladder is operated in manual.
Operators corrected gate positioning.


7/24, 7/25
A branch water over weir
Staff gauge reads >1.5’
Unknown
B-branch reads correctly, BI reads 1.2’ so no action taken.


7/24, 7/25
DSM2 orifice 13B-S
Not in correct position.
Proximity switches not functioning properly.
WAR turned in to the electricians.  
WAR# 20014417

7/27
FG3-33
Not in correct position for TW elevation.
Computer system not yet fully functional.
Operator manually closed diffuser.


4.3 Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

Date
Wash. Shore
Bradford Is.

7/22
19.2
19.1

7/23
19.6
19.4

7/24
19.9
19.8

7/25
20.2
20.1

7/26
20.3
20.2

7/27
20.3
20.1

7/28
20.4
20.1

4.4 Sensor Calibration.  Water level sensors were checked for calibration on 25 July.  

4.5 Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

5. MISCELLANEOUS

5.1 PH2 JBS injury/mortality issue: Juvenile mortality remains low at the JMF, according to PSMFC reports.  

5.2 Because of low tailwater elevations and the physical limits of the weir gates, entrance openings for PH1 Collection Channel are less than 8.0’.   Gate 64 has been reprogrammed to maintain at least an 8’ opening.  

5.3 Closed OG/SG testing causes low differential at the north end of PH1 collection channel.  FV1-1 normally controls south channel differential, but is now reprogrammed to maintain north channel differential.  This change should also help maintain proper collection channel velocity during OG/SG tests.  

5.4 The B-Branch computer was installed on 19 July.  As soon at the Entrance Pool elevation sensor has been calibrated and the North and South entrance gates are connected properly, B-Branch will be back in auto operation.  Until then, the entrance gates, FV4-3 and FV4-4 are operated in manual.

                                                                                                                DEBORAH L. CHENOWETH

                                 

                                                             Operations Project Manager

//S//

3
3

