 
CENWP-OP-B                                                                                                                           30 September, 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 39 of 2001, which covers the period 23 through 29 September.
1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 80.9 to 106.3kcfs.   Daily project tailwater elevation averaged 7.5’ to 9.6’ msl.  Daily project forebay elevation averaged 75.4’ to 75.8’ msl.  River temperature averaged 66 to 67° F.

1.2 Spill bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, remain open 4”.  This translates to a daily spill average of 2.3kcfs.

1.3 Unit 3 remains out of service for turbine rehab.  Unit 17 remains out of service for its four-year overhaul.  Unit 5 remains out of service for turbine rehab.  Unit 9 went out of service at 0642 on 24 September for Bank 9/10 work.  Unit 6 went out of service from 0700 until 1530 on 24 September for test equipment removal.

1.4 Second Powerhouse fish units remain in service.  They provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  

2.  ACTIVITIES. 
2.1 AWS Closures. FV4-3 and FV4-4 at B-branch and FV5-3 and FV5-4 are all operating in manual until the new computer system is calibrated.  FV5-9 was closed for cleaning from 1500 until 1506 on 27 September.  

2.2 STS/VBS Inspections.  No STSs were inspected this reporting week.
2.3 STS removal. PH1 STS remain OOS per NMFS request.

Unit
Date
Run Hours
Comments

1
9/4
48
Removed for season

2
9/4
26
Removed for season

3


Already out

4
9/5
7
Removed for season

5


Already out

6
9/13
364
Removed for season

7
9/15
279
Removed for season

8
9/10
ESBS
Removed for season

9
9/4
205
Removed for season

10
9/4
312
Removed for season

Table 1.  STS Removal Dates.

2.4 Dewatering and Fish Salvage.  No dewatering or fish salvage activities this reporting week.

3.  RESEARCH.

3.1 WDFW Fish Counting.  WDFW continues 16-hour visual counts and 8-hour video counts at Bradford Island and Washington Shore ladders.

3.2 NMFS Saltwater rearing. The Saltwater rearing facility is in operation.  Sampling May- November.

3.3 PSMFC Adult PIT.  Tagging began again on 18 September at the AFF.

3.4 PSMFC Smolt Monitoring Program.  Collection continues 24h/d at the PH2 monitoring facility. 

3.5 UI Adult Fallback. UI Adult Radiotracking/Tagging.  PCC entrance gates at the first powerhouse are being operated according to UI request until 31 October.  Tagging of Chinook began at the AFC&MF 2 April and will continue seven days a week until the end of September.   

3.6 CRITFC/ODFW/WDFW Adult Trapping/Tagging.  Tagging Chinook and steelhead two days a week.  

3.7 NMFS Lamprey.  Tracking continues.  Operation of the spillway ladders for lamprey test mode (.5’ differential) will end 30 September.

3.8 YIN Northern Pikeminnow Dam Angling.  Fishing 25 June – 30 September.

3.9 WDFW/ODFW Fall Chinook Counting.  Observations of the fall Chinook will end 30 September.

4.  FISHWAYS. 
4.1 Project biologists inspected 23 through 29 September this reporting week.   Salmon Corps volunteers inspected 23, 25, 26, 27, and 28 September. 

4.2 Fish Passage Plan Observations.

DATE
LOCATion
FPP Deviation
CAUSE
RESPONSE
TR/WAR

All week
PH2 collection channel electronic velocity meter.
The velocity meter is not yet working.
Not fully installed.
Working on final installation.


All week
FG3-28
Out of service
Manually closed because of displaced diffuser valve cover.
New covers are designed, and will be installed during winter maintenance.
20013904

All week
FG3-27
Not in correct position for TW elev.
FG3-27 is open to replace FG3-28.
No action taken.


9/23-25, 9/28-29
PH1 Collection channel velocity
Velocity meter registers less than 1.5 fps.
Water backs up in the channel during OG/SG tests.  
Monitoring situation.


All week
Main Dam Avian wires
Wires removed.
Spillway deflector installation.
Wire grid to be replaced in Mid-April.


9/24 
Weir 37 
Reading 1.5’
Unknown (please see misc. 5.6)
Operators corrected problem.


4.3 Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

Date
Wash. Shore
Bradford Is.

9/23
19.1
19.1

9/24
19.2
19.2

9/25
19.4
19.3

9/26
19.3
19.3

9/27
19.1
19.1

9/28
19.0
19.0

9/29
18.9
18.9

4.4 Sensor Calibration.  Water level sensors were checked for calibration on 28 September.  

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

5. MISCELLANEOUS

5.1 PH2 JBS injury/mortality issue: Juvenile mortality remains low at the JMF, according to PSMFC reports.  

5.2 Because of low tailwater elevations and the physical limits of the weir gates, entrance openings for PH1 Collection Channel are less than 8.0’.   Gate 64 has been reprogrammed to maintain at least an 8’ opening.  

5.3 Closed OG/SG testing causes low differential at the north end of PH1 collection channel.  FV1-1 normally controls south channel differential, but is now reprogrammed to maintain north channel differential.  This change should also help maintain proper collection channel velocity during OG/SG tests.  

5.4 The B-Branch and Cascade Island computers were installed.  Sensors need calibrated and some parameters need setting.  Until then, entrance gates and FV4-3, 4-4, 5-3, and 5-4 are operated in manual.  Waiting on parts.

5.5 Salmon Corps finished their volunteer work at Bonneville on 28 September.

5.6 The stillwell for weir 37 float control has a floor in it.  This prevents it from controlling much below 1.1’ of water over the weir.  Considering redesigning the stillwell.  

5.7 The outfall hydrocannon remains off.  We have not observed any bird activity.

                                                                                                                DEBORAH L. CHENOWETH

                                 

                                                             Operations Project Manager

//S//

3
3

