 
CENWP-OP-B                                                                                                                               28 October, 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 43 of 2001, which covers the period 21 through 27 October.
1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 75.2 to 107.0kcfs.   Daily project tailwater elevation averaged 7.5’ to 9.2’ msl.  Daily project forebay elevation averaged 72.3’ to 75.5’ msl.  River temperature averaged 58 to 60° F.

1.2 Spill bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, remain open 4”.  This translates to a daily spill average of 2.3kcfs.

1.3 Units 3 and 5 remain out of service for turbine rehab.  Station service Unit 0 remains out of service.  Unit 15 remains out of service for a 4-yr overhaul.  

1.4 Second Powerhouse fish units remain in service.  They provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.    

2.  ACTIVITIES. 
2.1 AWS Closures.   The following dates and times are when the respective valves were closed for cleaning.  

22 October, FV3-9 from 1325 until 1332; 

25 October, FV1-1from 1504 -1511, FV3-9 from 1516 -1528, BI Fish exit from 1520 -1527; 

27 October, FV5-9 from 1145 until 1200, FV3-9 from 1229 until 1245; 

2.2 STS/VBS Inspections.  No STSs were video inspected this reporting week.

2.3 STS removal. PH1 STS remain OOS per NMFS request.

2.4 Dewatering and Fish Salvage.  No dewater or fish salvage activities to report.

3.  RESEARCH.

3.1 WDFW Fish Counting.  Continued 16 hour visual counts and 8 hour video counts at BI and WA. Shore.

3.2 NMFS Saltwater rearing. The Saltwater rearing facility is in operation.  Sampling May- November.

3.3 PSMFC Adult PIT.  Planning for construction at the Bradford Island and Cascade Island ladders continues.

3.4 PSMFC Smolt Monitoring Program.  Collection continues 24h/d at the PH2 monitoring facility. 

3.5 UI Adult Fallback. PCC entrance gates at PH1are operated according to UI request until 31 October.    

3.6 ODFW/WDFW Adult Trapping/Tagging.  Tagging ended on 23 October.

4.  FISHWAYS. 
4.1 Project biologists inspected 21, 22, 24-27 October this reporting week.

4.2 Fish Passage Plan Observations.

DATE
LOCATion
FPP Deviation
CAUSE
RESPONSE
TR/WAR

All week
PH2 collection channel electronic velocity meter.
The velocity meter is not yet working.
Not fully installed.
Working on final installation.


All week
FG3-28
Out of service
Manually closed because of displaced diffuser valve cover.
New covers will be installed during winter maintenance.
20013904

All week
FG3-27
Not in correct position for TW elev.
FG3-27 is open to replace FG3-28.
See above.


10/21-22, 10/24-25
PH1 PCC velocity
Velocity meter registers <1.5 fps.
Water backs up in the channel during OG/SG tests.  
Monitoring situation.


All week
Main Dam Avian wires
Wires removed.
Spillway deflector installation.
Grid to be replaced in Mid-April.


10/27
CI entrances
Not in correct position for TW elev.
Entrance gates are operated manually.
Operators adjusted gates.


10/24-25, 10/27
B-Branch entrances
Not in correct position for TW elev.
Entrance gates are operated manually.
Operators adjusted gates.


10/21-24, 
Weir 37
Reading >1.1’
 See misc. 5.5
No action taken at this time.


4.3 Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

Date
Wash. Shore
Bradford Is.

10/21
15.1
15.0

10/22
14.7
14.7

10/23
14.3
14.1

10/24
13.9
13.7

10/25
13.9
13.7

10/26
13.8
13.6

10/27
13.7
13.5

4.4 Sensor Calibration.  Water level sensors were checked for calibration on 26 October.  

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

5. MISCELLANEOUS

5.1 PH2 JBS injury/mortality issue: Juvenile mortality remains low at the JMF, according to PSMFC reports.  

5.2 Because of low tailwater elevations and the physical limits of the weir gates, entrance openings for PH1 Collection Channel are less than 8.0’.   Gate 64 has been reprogrammed to maintain at least an 8’ opening.  

5.3 Closed OG/SG testing causes low differential at the north end of PH1 collection channel.  FV1-1 normally controls south channel differential, but is now reprogrammed to maintain north channel differential.  This change should also help maintain proper collection channel velocity during OG/SG tests.  

5.4 The B-Branch and Cascade Island computers were installed.  Until sensors have been calibrated, entrance gates, diffusers, valves FV4-3, FV4-4, FV5-3, FV5-4 are operated in manual.

5.5 Weir 37 float control doesn’t adequately control water level over the weir.  A sonic transducer will be installed this winter, which should correct the problem.  

5.6 The outfall hydrocannon remains off.  We have not observed any bird activity.

5.7 PH2 ITC was open from 0830 until 1580 on 22 October.

5.8 Valve 12 at the Adult Fish Facility broke on 23 October.  It was back in service on 25 October.

5.9 USGS hydroacoustically inspected the old navigation lock for fish on 25 October.  They reported seeing very few.

5.10 Advanced American Divers reported a 5-8 gallon oil spill at their work site at the Main Dam around 1300 on 26 October.  No oil was reported to have entered the water, the contractors did the cleanup.
                                                                                                                DEBORAH L. CHENOWETH

                                 

                                                             Operations Project Manager

//S//

1
2

