
CENWP-OP-B                                                                                                                                  04 March, 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 09 of 2002, which covers the period 24 February through 02 March 2002.
1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 129.8 to 163.3kcfs.  Daily project tailwater elevation averaged 12.7’ to 14.8’ msl.  Daily project forebay elevation averaged 74.4’ to 75.4’ msl.  River temperature averaged 45 to 46° F.  Daily turbidity averaged 5.6 to  >7’ on the secchi disk.

1.2 Spill Bays 18 and 1 are closed for spill deflector work.  

1.3 Unit 5 remains out of service for turbine rehab.  Unit 17 remains out of service for VBS slot modification work.   Unit 3 returned to service at 1912 on 28 February.  Unit 10 went out of service at 0712 on 26 February for digital governor installation and a five- year overhaul.  Unit 11 went out of service 0400 on 27 February for a lower guide bearing oil leak repair.

Units out of service for trash rack raking: 

28 February- Unit 8 (0648- 1318), Unit 16 (1012- 1100), Unit 15 (1100- 1148), Unit 18 (1230- 1406)

     Unit 7 (1318- 1542), Unit 13 (1448- 1612)

Units out of service for research transducer installation:

25 February- Unit 7 (0648- 0954) and Unit 9 (1000- 1424)

Units out of service for STS or ESBS installation:

27 February- Unit 8 (0742- 1418)

01 March- Unit 9 (0636- 0912), Unit 6 (0912- 1118), Unit 4 (1118- 1348), Unit 3 (1348- 1630)

02 March- Unit 2 (0654- 0848), Unit 1 (0848- 1136)

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly, if drawdown exceeds 1.0’.  Fish Unit 1 remains out of service for winter maintenance.  Fish Unit 2 returned to service at 1430 on 28 February.
1.5 Gatewell Drawdown was measured on 27 February.  All units were within criteria.
2.  ACTIVITIES. 
2.1 AWS Closures. 

All Cascade Island AWS valves are closed for winter maintenance.

01 March- FV3-9 was closed for cleaning from 1600 until 1630.

02 March- FV3-7 was closed for cleaning from 1450 until 1515




FV1-1 was closed for cleaning from 1537 until 1610.

2.2 STS/VBS Inspections.  All DSM1 STSs have been installed for fish passage season.

2.3 Dewatering and Fish Salvage.   Cascade Island was completely dewatered for repair to a blown diffuser cover.  No fish were found.   On 26 February, biologists removed 24 peamouth from the Adult PIT tag detector installation area.  They had collected behind the contractor sandbags.  All fish were released in the tailrace in good condition.

3.  RESEARCH.

3.1 WDFW Fish Counting.  24-hour video count ongoing at the Bradford Island and Washington Shore ladders.

3.2 PSMFC Adult PIT.  Installation underway at Cascade Island ladder.  Non in-water work ongoing at Bradford Island. 

3.3 PSMFC/NMFS Juvenile PIT.  The flat plate detector was returned to DSM1 on 20 February. 

3.4 WDFW Winter Steelhead tagging.  Trapping began 01 March.

3.5 NMFS Lamprey.  Tracking continues. 

4.  FISHWAYS. 
4.1 Project biologists inspected 25-28 February and 01 March this reporting week.

4.2 Fish Passage Plan Observations.

DATE
LOCATion
FPP Deviation
CAUSE
RESPONSE
TR/WAR

2/26-28, 3/1
PH1 PCC velocity
Velocity <1.5fps on the electronic meter.
Unknown



2/28
Weir 37
Reading <1.0’
Unknown.  
Operators to check.


2/28-3/1
PH2 PCC velocity meter.
Electronic meter not yet installed.
Divers weren’t able to install parts during 19 February dive.
The transducer will be installed on 13 March.


3/1
PH2 DSM
DSM out of service
ERG seal repair work.  STS installation.
The ERG seal was repaired on 02 March.  See misc. 5.6


4.3 Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperature will be recorded beginning 04 March.

4.4 Sensor Calibration.  Calibration was checked on 26 February this reporting week.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

5. MISCELLANEOUS

5.1 The B-Branch and Cascade Island computers were installed, though we still wait on brackets for the transducers.  Until brackets are installed, FV4-3, FV4-4, FV5-3, FV5-4 are operated in manual.

5.2 To aid spawning Chum below Bonneville, a minimum tailwater restriction of 11.4’ went into effect at 1054 on 28 November.  The restriction will continue until further notice.

5.3 DSM1 returned to service at 1515 on 26 February.  The inclined screen continuously cycled all the way up and all the way down.  The DSM was turned south at 1701 on 26 February.  Repairs were made to the PLC and the DSM was returned to normal operation at 0900 on 27 February.

5.4 Washington Shore returned to service at 1030 on 28 February.  The AFF returned to bypass conditions at 1847 on 28 February.  The UMT and Cascade Island are not scheduled to return until 08 March.

5.5 The ERG seal was repaired on 02 March.  It was originally not anticipated to be ready until 07 March.

5.6  DSM2 is scheduled to return to service the week of 03 March.  STSs and TIES will be installed early in the week.

 DEBORAH L. CHENOWETH

                                 

                                                             Operations Project Manager

//S//

1
2

