
CENWP-OP-B                                                                                                                                  28 May, 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 21 of 2002, which covers the period 19 through 25 May 2002.
1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 229.1 to 293.6kcfs.  Daily project tailwater elevation averaged 17.9’ to 21.8’ msl.  Daily project forebay elevation averaged 75.5’ to 76.1’ msl.  River temperature averaged 54 to 56° F.  Daily turbidity measured 3.7 to 5.1’ on the secchi disk.

1.2 Spill Bays 1and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are operational and included in the spill pattern.  Spill averaged 81.6 to 151.1kcfs for the week.  

1.3 Unit Operation
1.3.1 Unit 1 was out of service from 0400 on 21 May until 1518 on 23 May for pre rehab testing.

1.3.2 Unit 2 remains out of service for digital governor and exciter work.  

1.3.3 Unit 5 remains out of service for turbine rehab.  

1.3.4 Unit 7 was out of service from 1600 until 2018 on 22 May due to a STS failure.

1.3.5 Unit 9 went out of service at 2400 on 19 May for digital governor work and a five year overhaul.

1.3.6 Unit 11 went out of service at 2330 on 24 May due to a STS failure.

1.3.7 Unit 15 remains out of service until the VBSs are repaired (see misc. 5.4)

1.3.8 Unit 17 was out of service for FGE testing 20-23 May.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.   F1 was out of service from 0706 on 22 May until 1248 on 23 May for exciter maintenance and to allow a contractor to take stator measurements. 

1.5 Gatewell drawdowns were measured on 22 May.

2.  ACTIVITIES. 
2.1 AWS Closures.  The following AWSs were closed for cleaning.

22 May- BI exit from 1510 until 1540
2.2 STS/VBS Inspections.  No STSs/VBSs  inspections this week.

2.3 Dewatering and Fish Salvage.  Unit 9 draft tube was dewatered on 21 May for a five year overhaul.  One juvenile salmonid and 1 dead two foot sturgeon were removed.  The fish were returned to the tailrace.

3.  RESEARCH.

3.1 CRITFC Age and Length Composition.  Collected 40 Spring Chinook this reporting week.

3.2 NMFS FGE.  Unit 17 FGE study is underway.   NO FGE test on 13 May because of VBS failures.

3.3 NMFS Lamprey.  Tracking continues.   Collection begins 28 May.

3.4 NMFS Saltwater Rearing.  Collection and rearing continue. 

3.5 Normandeau Balloon-tag at Spillway.  Study to run 20 May – mid June and 1-15 August.

3.6 OCFWRU Transportation Study.  Study of post-transportation migration and survival of juveniles to run 29 April through 14 July.

3.7 ODFW Summer Steelhead sampling.  Sampling 2 days/week 8 hours/day.  Will sample 1% of the run.

3.8 Pelfrey Sturgeon Hatchery.  Capturing broodstock May 24 – June 24.

3.9 PSMFC Adult PIT.  Detectors are installed in all ladders.  Some of the detectors have developed leaks and will be monitored throughout the season.  Repairs are scheduled for 2002-03 winter maintenance season.

3.10 PSMFC JMF.  Monitoring continues.

3.11 PSMFC/NMFS Juvenile PIT.  Monitoring continues.

3.12 U of I Adult Radio tracking.  Trapping began 1 April and will continue 7 days/week until October.  One mortality on 25 May.  See misc. 5.7.
3.13 U of I Transportation Study.  Evaluation of physiological condition of river run v. barged Snake River juveniles to occur May-June.  May add separation–by-code study June-August.

3.14 USGS EMG studies.  Tissue samples will be taken from 200 Chinook 1 April through June.

3.15 USGS Juvenile Radio tracking.  Study in progress.

3.16 USGS Lamprey.  Collection of lamprey at the AFF began in May.

3.17 USGS MGR.  Began 4 May, but low river flows are interrupting the study. 

3.18 USGS Sort by Code.  Length and weight are recorded and fish are released back to the river.

3.19 WDFW Fish Counting.  16-hr visual and 8-hr video counts at Bradford Island and Washington Shore.

3.20 WDFW Jaw tagging.  Tagging 50-75 fish per week as control for tangle net study.

3.21 WDFW Winter Steelhead Tagging.  Trapping and tagging steelhead once a week.

3.22 WES/Battelle/Mevatech Juvenile Hydroacoustics.  Study in progress.  

3.23 WES Spillway Deflector Testing.  WES will monitor water quality equipment to determine effectiveness of new flip lips.  Study began with initiation of spill on 10 April.

4.  FISHWAYS 
4.1 Project biologists inspected 19, 21-24 May this reporting week.  

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR/WAR

	All week
	PH1 PCC velocity
	Velocity <1.5fps on the electronic meter.
	Unknown- the rest of the ladder is in criteria.
	No action at this time.
	

	5/20, 5/25
	
	Biologists did not inspect 7 days/ week.
	Personnel shortage.
	Job advertised.
	

	All week
	B-Branch
	FG3-25
	Broken shaft.
	An adjacent diffuser is opened.
	

	All week
	DSM2
	Add in valve closed.
	Gaps in VBSs at Unit 15 and 17.
	Valve closed until VBSs are repaired (see misc. 5.4)
	

	5/21
	SMF
	Lower switchgate not in correct position for TW elevation.
	Faulty indicator switch.
	Crews worked on gate, it will switch but indication is still incorrect.
	TR#7227

	5/22
	Cascade Island
	Diffusers not in correct position for TW elevation.
	Ladder entrance still in manual mode.
	Operators corrected diffusers.
	

	5/22
	PH1 PCC
	OG 62 not controlling in auto.
	Unknown.  
	Operators turned in TR and manually adjusted the gate.
	

	5/23
	B-branch 
	Diffusers not in correct position for TW elevation.
	Ladder entrance still in manual mode. 
	Operators corrected diffusers.
	


4.3 Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are Reaumurs this week.  This scale is named after the French scientist Rene Antoine Ferchault de Reaumur, a discoverer of fabricating steel from iron, artificial egg incubation and an authority on the natural history of insects.   

	Date
	Wash. Shore
	Bradford Is.

	5/19
	10.0
	10.08

	5/20
	10.16
	10.16

	5/21
	10.24
	10.32

	5/22
	10.4
	10.4

	5/23
	10.4
	10.48

	5/24
	10.56
	10.56

	5/25
	10.8
	10.88


4.4 Sensor Calibration.  Calibration was checked on 22 May this reporting week.  Everything is within criteria.

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

5. MISCELLANEOUS

5.1 B-branch and Cascade Island are operated in manual mode until stillwells can be installed for the tailwater sensors.  Installation will wait until spill has concluded.

5.2 Turbulent flows from spillbays 1 and 18 enter the side entrance gates of Cascade Island and Bradford Island B-branch ladders, causing poor entrance conditions.  District hydraulic engineers are investigating the problem.  On 3 May, the structural crew installed a bulkhead in the side entrance at Cascade Island.  Entrance conditions improved.  CG funds will be used to build a bulkhead for Bradford Island B-branch.

5.3 Sighting of sea lions and harbor seals in the tailrace of both powerhouses and the spillway have ceased.  One sea lion was locked through and it now in the forebay.  Attempts will be made to encourage it into the locks and move out downstream.  FFU continues to monitor the tailrace for any signs of marine mammals.

5.4 An adult steelhead was seen behind the add in water bars in DSM2 on 08 May.  VBSs were immediately video inspected.  Upon dewatering U17 A-slot, the VBS was found to have crumpled in towards the scroll case.   VBSs from U15 were moved to U17 so that FGE testing could continue.  U15 will be out of service until new VBSs are made for that unit.

5.5 SMF hydrocannons were turned off from 1800 until 2000 on 21 May to facilitate avian wire placement at the end of the outfalls.

5.6 PH2 Ice and trash chute was in operation from 0800 until 1700 flushing debris from the forebay.

5.7 On 23 May 2002, PSMFC reported an increase in juvenile mortalities at the JMF.  The fish were coming into the facility dead, but with no apparent injuries.  PSMFC will notify us if this becomes a trend or if fish start exhibiting notable injuries or marks.

5.8 On 25 May 2002 a chinook salmon mortality occurred during the daily tagging effort at the AFF. The fish was an unmarked chinook.  An identifying PIT tag, 526C420850, determined that it was originally PIT tagged by NMFS on 24 Apr. 1999 at LGR.  PIT tag information denoted that it was a wild chinook of unknown origin.  The fish was radio tagged at 11:18, following established radio-tagging procedures.  The fish fully recovered from anesthesia and was active in the transport tank.  Approximately one hour after tagging, the fish began to appear lethargic. The fish was revived by manually gilling it in the water until it again seemed fully recovered.  Several minutes later the fish was lethargic again. Repeated attempts to revive the fish failed. At this point the fish was starting to lose color in body and gills. It ceased to gill at 13:27.

 DEBORAH L. CHENOWETH

                                 

                                                             Operations Project Manager

//S//

1
3

