
CENWP-OP-B                                                                                                                                  15 July, 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 28 of 2002, which covers the period 07 through 13 July 2002.

1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 216.7 to 260.8kcfs.  Daily project tailwater elevation averaged 17.7’ to 20.3’ msl.  Daily project forebay elevation averaged 74.6’ to 75.6’ msl.  River temperature averaged 62 to 64° F.  Daily turbidity measured 4.0’ to 7.0’ on the secchi disk.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are operational and included in the spill pattern.  Spill averaged 84.7 to 120.2kcfs.  

1.3 Unit Operation

1.3.1 Unit 1 remains out of service for turbine rehab.

1.3.2 Unit 2 was out of service from 0700 until 0800 on 09 July for digital governor work.

1.3.3 Unit 3 was out of service from 1242 until 1342 on 09 July for digital governor work.

1.3.4 Unit 4 went out of service at 0424 on 08 July for digital governor work.

1.3.5 Unit 5 remains out of service for turbine rehab.  

1.3.6 Unit 12 remains out of service due to exciter failure, which occurred on 03 July.

1.3.7 Unit 13 was out of service from 1500 until 1542 on 09 July to facilitate troubleshooting of unit 12.

1.3.8 Unit 17 was out of service for FGE testing from about 1600 until 2100 from 08-11 July.  VBSs were cleaned during swing shift on FGE test nights.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  On 09 July, both Fish units were out of service from 0630 until 1536 (for F1) and 1618 (for F2) due to the dive at PH2 and for slipring work.

1.5 Gatewell drawdowns were measured every day for Unit 17 and on 11 July for the rest of the units.

2.  ACTIVITIES. 
2.1 AWS Closures.  The following AWS valves were closed for cleaning;

10 July- FV3-9 from 1510 until 1530, FV1-1 from 1537 until 1545.

2.2 STS/VBS Inspections.  The following STS/VBSs were inspected this reporting week.

	Unit
	Date
	Run Hours
	Comments

	11
	7/02
	504
	Repaired STS # 4 in 11-A, rips around rivets and a splice came apart, 

Repaired VBS in 11-A, replaced a previous patch.

	12
	7/11
	530
	

	13
	7/11
	526
	

	14
	7/11
	675
	

	15
	7/12
	488
	

	16
	7/12
	676
	

	17
	7/12
	583
	

	18
	7/12
	668
	


Table 1.  STS Inspection Dates.

2.3 Dewatering and Fish Salvage.  The bulkhead for DSM1 went in at 0700 on 08 July to facilitate repair of the Add-in valve.  Biologists removed 3 subyearling Chinook and 2 sculpin.  All fish were released downstream.

3.  RESEARCH.

3.1 CRITFC Age and Length Composition.  Collected 80 Chinook and 111 Sockeye this reporting week.

3.2 NMFS FGE.  Unit 17 FGE study is ongoing.  Summer tests were completed on 11 July.

3.3 NMFS Lamprey.  The lamprey flume is in operation at the Bradford Island AWS channel.  Collection and tracking continue.

3.4 NMFS Saltwater Rearing.  Collection and rearing continue. 

3.5 Normandeau Balloon-tag at Spillway.  Low flow study commences in August.

3.6 OCFWRU Transportation Study.  Study of post-transportation migration and survival of juveniles to run 29 April through 14 July.

3.7 ODFW Summer Steelhead sampling.  Sampling 2 days/week 8 hours/day.  Will sample 1% of the run.

3.8 PSMFC Adult PIT.  Detectors are installed in all ladders.  Some of the detectors have developed leaks and will be monitored throughout the season.  Repairs are scheduled for 2002-03 winter maintenance season.

3.9 PSMFC JMF.  One dead kelt was removed from the separator bars.  Recorded as going over the bars were 27 steelhead, 7 salmon and 1 unknown salmonid fallbacks and 68 smolts.  
3.10 PSMFC/NMFS Juvenile PIT.  104 sub yearling Chinook were examined for GBT this week.

3.11 U of I Adult Radio tracking.  Trapping began 1 April and will continue 7 days/week until October.

3.12 U of I Transportation Study.  Evaluation of physiological condition of river run v. barged Snake River juveniles to occur June-September.

3.13 USGS Juvenile Radio tracking.  Study in progress.

3.14 WDFW Fish Counting.  16-hr visual and 8-hr video counts at Bradford Island and Washington Shore.

3.15 WES/Battelle/Mevatech Juvenile Hydroacoustics.  Study in progress.  

3.16 WES Spillway Deflector Testing.  WES monitoring water quality equipment to determine effectiveness of new flip lips.  Study began with initiation of spill on 10 April.

3.17 Yakama Dam Angling.  YIN began angling for pikeminnows at Bonneville on 1 July.  

4.  FISHWAYS 
4.1 Project biologists inspected 08-12 July this reporting week.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR/WAR

	7/9-12
	PH1 PCC velocity
	Velocity <1.5fps on the electronic meter.
	Unknown
	No action at this time.
	

	All week
	Main dam
	Two avian wires broken.
	Vandalism
	No action taken at this time.
	

	7/7, 7/13
	
	Biologists did not inspect 7 days/ week.
	Personnel shortage.
	Training a new employee.
	

	7/8-9
	PH2 PCC velocity
	Velocity <1.5fps on the electronic meter.
	Dives
	No action taken at this time.
	

	7/7
	DSM1
	Water levels out of criteria
	Add in valve malfunction.
	Channel turned south.  See misc 5.4
	TR# 8209

	7/7
	Unit 12
	Orifices 12A-S and C-S OOS
	Mounting bolt broken.
	TR submitted.  See misc. 5.5
	TR#8213


4.3 Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius.

	Date
	Wash. Shore
	Bradford Is.

	7/07
	17.8
	17.8

	7/08
	17.9
	17.9

	7/09
	17.9
	17.9

	7/10
	18.0
	17.9

	7/11
	18.3
	18.2

	7/12
	18.6
	18.6

	7/13
	18.8
	18.8


4.4 Sensor Calibration.  Calibration was checked on 12 July this reporting week.  

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

5. MISCELLANEOUS

5.1 B-branch and Cascade Island are operated in manual mode until stillwells can be installed for the tailwater sensors.  Installation will wait until spill has concluded.

5.2 Turbulent flows from spillbays 1 and 18 enter the side entrance gates of Cascade Island and Bradford Island B-branch ladders, causing poor entrance conditions.  District hydraulic engineers are investigating the problem.  On 3 May, the structural crew installed a bulkhead in the side entrance at Cascade Island.  Entrance conditions improved.  CG funds will be used to build a bulkhead for Bradford Island B-branch.

5.3 There had been some difficulty in maintaining an opening for fish at PH1 weir gate 1.  Electricians recalibrated the gates and at this time there does not appear to be a problem.

5.4 Due to a continually cycling Add in valve, DSM1 was turned south from 1430 on 04 July until 1040 on 08 July.  The valve continued to cycle and attempt to back flush but to no avail.  Operators tried the air burst system but that too failed to clear the valve for any length of time.  In the interest of fish safety, it was decided that the channel should be turned south until repairs could be made the morning of 08 July.  No mechanical problems were found with the valve.
5.5 Due to broken mounting bolts at orifices 12A-S and 12C-S, the orifices were in manual and closed from 1430 on 06 July until 1420 on 10 July.  It was believed that orifice cycling would cause further damage.  Channel elevation remained in criteria. 

5.6 On 08 July, the mid season dive occurred for PH1.  PH2 was done on 09 July.  There were no significant findings.

5.7 PSMFC reported the upper switchgate automatically switched to bypass at the SMF on the evening of 08 July.  On 09 July, electricians went to inspect and found no problems.  The upper switchgate moves to bypass if manually switched or in the event of a power outage.  Neither of which were reported as occurring.

 DEBORAH L. CHENOWETH

                                 

                                                             Operations Project Manager

//S//

1
3

