
CENWP-OP-B                                                                                                                                  12 August 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 32 of 2002, which covers the period 04 through 10 August 2002.

1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 151.2 to 181.6kcfs.  Daily project tailwater elevation averaged 12.9’ to 15.7’ msl.  Daily project forebay elevation averaged 74.8’ to 75.7’ msl.  River temperature averaged 66 to 67° F.  Daily turbidity measured 5.0’ to 7.0’ on the secchi disk.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are operational and included in the spill pattern.  Spill averaged 87.6 to 143.5kcfs.  

1.3 Unit Operation

1.3.1 Unit 1 remains out of service for turbine rehab.

1.3.2 Unit 5 remains out of service for turbine rehab.  

1.3.3 Unit 7 returned to service at 1200 on 07 August.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  

1.5 Gatewell drawdowns were measured on 07 August.

2.  ACTIVITIES. 
2.1 AWS Closures.  No AWS valves were closed.

2.2 STS/VBS Inspections.  The following STS/VBSs were inspected this reporting week.

	Unit
	Date
	Run Hours
	Comments

	11
	8/7
	856
	

	18
	8/7
	688
	


Table 1.  STS Inspection Dates.

2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage activities this reporting week.

3.  RESEARCH.

3.1 CRITFC Age and Length Composition.  Collected 28 chinook this reporting week.  Will collect one day a week until the fall run increases.

3.2 NMFS Lamprey.  The lamprey flume is in operation at the Bradford Island AWS channel.  Radio tagging has concluded, tracking continues.

3.3 NMFS Saltwater Rearing.  Mortality is increasing.  Specific data available from Lyle Gilbreath. 

3.4 Normandeau Balloon-tag at Spillway.  Low flow study commences 18 August.

3.5 ODFW Summer Steelhead sampling.  Sampling 2 days/week 8 hours/day.  Will sample 1% of the run.

3.6 PSMFC Adult PIT.  Detectors are installed in all ladders.  Some of the detectors have developed leaks and will be monitored throughout the season.  Repairs are scheduled for 2002-03 winter maintenance season.

3.7 PSMFC JMF.  One steelhead went over the separator bars.  GBT exams were performed on 154 sub-yearling Chinook.

3.8 PSMFC/NMFS Juvenile PIT.  DSM1 flow is running south.

3.9 U of I Adult Radio tracking.  Trapping began 1 April and will continue 7 days/week until October.

3.10 U of I lamprey testing.  The AFF lamprey flume is in operation.  Tests ongoing.

3.11 U of I Transportation Study.  Evaluation of physiological condition of river run v. barged Snake River juveniles to occur June-September.

3.12 USGS Juvenile Radio tracking.  In most locations radio tracking completed.

3.13 WDFW Fish Counting.  16-hr visual and 8-hr video counts at Bradford Island and Washington Shore.

3.14 WES/Battelle/Mevatech Juvenile Hydroacoustics.  Study completed.  

3.15 WES Spillway Deflector Testing.  WES monitoring water quality equipment to determine effectiveness of new flip lips.   

3.16 Yakama Dam Angling.  YIN began angling for pikeminnows at Bonneville on 1 July.  

4.  FISHWAYS 
4.1 Project biologists inspected 05-10 August this reporting week.  

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR/WAR

	8/5-9
	PH1 PCC velocity
	Velocity <1.5fps on the electronic meter.
	Unknown
	No action at this time.
	

	All week
	Main dam
	Two avian wires broken.
	Vandalism
	Will be repaired this winter maint. season.
	

	8/04
	
	Biologists did not inspect 7 days/ week.
	Personnel shortage.
	Training a new employee.
	

	8/7-9
	PH2 PCC velocity
	Velocity <1.5fps on the electronic meter.
	Low tailwater causes an inaccurate reading.
	Sensor relocation this winter maint. Season.
	


4.3 Fish Ladder Temperatures.  Measurements are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius.  

	Date
	Wash. Shore
	Bradford Is.

	8/4
	20.3
	See misc. 5.6

	8/5
	20.1
	

	8/6
	20.1
	

	8/7
	20.0
	

	8/8
	20.2
	

	8/9
	20.3
	

	8/10
	20.6
	


4.4 Sensor Calibration.  Checked calibration on 06 August this week.  

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

5. MISCELLANEOUS

5.1 B-branch and Cascade Island are in manual mode until tailwater stillwells can be installed this winter.

5.2 Turbulent flows from spillbay 18 enter the side entrance gate of Bradford Island B-branch ladder, causing poor entrance conditions.  CG funds will be used to build a bulkhead for B-branch.

5.3 During low tailwater, the PH2 monoliths are unable to maintain greater than 13’ openings.  

5.4 PH2 ice and trash chute bulkhead was removed for debris removal from 0712 on 07 August until 1300 on 08 August.

5.5 TIES removal was completed on 08 August.

5.6 The Bradford Island temperature probe is out of service.  The probe’s failure may explain last week’s temperature difference between the two ladders (see report 0231).  We moved the Washington shore back up probe to Bradford Island on 12 August.  We will either purchase new probes or obtain temperature monitoring attachments for our existing velocity meters.  The digital temperature probe at the AFF appears to be out of calibration as well.  We cannot recalibrate it until the lab is dewatered this winter.  University of Idaho is using a thermometer to track temperatures.

 DEBORAH L. CHENOWETH

                                 

                                                             Operations Project Manager

//S//

1
3

