
CENWP-OP-B                                                                                                                            03 September 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 35 of 2002, which covers the period 25 through 31 August 2002.

1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 135.8 to 159.4kcfs.  Daily project tailwater elevation averaged 11.7’ to 12.9’ msl.  Daily project forebay elevation averaged 73.9’ to 75.9’ msl.  River temperature averaged 66 to 67° F.  Daily turbidity measured 3.0’ to 7.0’ on the secchi disk.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are operational and included in the spill pattern.  Spill averaged 54.2 to 120.6kcfs.  Main dam went on seal at 2359 on 31 August.  

1.3 Unit Operation

1.3.1 Unit 1 remains out of service for turbine rehab.

1.3.2 Unit 5 remains out of service for turbine rehab.

1.3.3 Unit 13 was out of service for annual maintenance from 0500 until 1630 on 26 August.

1.3.4 Unit 14 was out of service for annual maintenance from 0500 until 2000 on 27 August.

1.3.5 Unit 15 was out of service for annual maintenance from 0500 until 1648 on 28 August.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

1.5 Gatewell drawdowns were measured on 28 August.

2.  ACTIVITIES. 
2.1 AWS Closures.  No AWS closures this reporting week.

2.2 STS/VBS Inspections. Three STS/VBSs were inspected this reporting week.  Here is a summary of all STS/VBSs at PH1.

	Unit
	Date
	Run Hours
	Comments

	1
	6/10
	397
	Unit out of service

	2
	8/28
	548
	

	3
	6/20
	680
	Dogged on deck.

	4
	6/20
	551
	Dogged on deck.

	5
	
	
	Unit out of service

	6
	6/19
	785
	Dogged on deck.

	7
	6/19
	867
	Dogged on deck.

	8
	2/27
	778
	

	9
	8/28
	455
	

	10
	8/28
	497
	


Table 1.  STS Inspection Dates.

2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage activities this reporting week.

3.  RESEARCH.

3.1 CRITFC Age and Length Composition.  Collected 98 chinook and eight coho this reporting week.  Will collect one day a week until the fall run increases.

3.2 NMFS Lamprey.  The lamprey flume is in operation at the Bradford Island AWS channel.  Radio tagging has concluded, tracking continues.

3.3 NMFS Saltwater Rearing.  Rearing continues.  Specific data available from Lyle Gilbreath. 

3.4 Normandeau Balloon-tag at Spillway.  Low flow study 18 August – 31 August. 

3.5 ODFW Summer Steelhead sampling.  Sampling 2 days/week 8 hours/day.  Will sample 1% of the run.

3.6 PSMFC/NMFS Adult PIT.  Detectors are installed in all ladders.  Some of the detectors have developed leaks and will be monitored throughout the season.  Repairs are scheduled for 2002-03 winter maintenance season.  Tagging occurred on 27 and 29 August.

3.7 PSMFC JMF.  The drive shaft for the PDS screen cleaner failed on 26 August.  The screen is cleaned manually (see misc 5.8).  167 sub yearling chinook were examined for signs of GBT.  Two steelhead and two salmon were recorded as fallback over the separator bars.

3.8 PSMFC/NMFS Juvenile PIT.  DSM1 flow is running south.

3.9 U of I Adult Radio tracking.  Trapping began 1 April and will continue 7 days/week until October.  Reported a fish mortality on 29 August.  (see misc. 5.10)
3.10 U of I lamprey testing.  The AFF lamprey flume is in operation.  Tests ongoing.

3.11 U of I Transportation Study.  Evaluation of physiological condition of river run v. barged Snake River juveniles concluded this week.

3.12 WDFW Fish Counting.  16-hr visual and 8-hr video counts at Bradford Island and Washington Shore.

3.13 WES Spillway Deflector Testing.  WES monitoring water quality equipment to determine effectiveness of new flip lips.   TDG tests scheduled for 24-29 August.

4.  FISHWAYS 
4.1 Project biologists inspected 25-29 August this reporting week.  

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR/WAR

	All week
	Main dam
	Two avian wires broken.
	Vandalism
	Will be repaired this winter maint. season.
	

	8/25-26, 8/28-29
	Weir 37
	Reading >1.0’
	In manual
	Operators to adjust.
	

	All week
	PH2 PCC velocity
	Velocity <1.5fps on the electronic meter.
	Low tailwater causes an inaccurate reading.
	Sensor relocation this winter maint. Season.
	

	8/27
	A and B branches
	Reading >1.0’
	Still in shad passage mode.
	Electricians to correct on 8/28
	

	8/30-31
	
	Biologists did not inspect 7 days/ week.
	Personnel shortage.
	Training a new employee.
	


4.3 Fish Ladder Temperatures.  Measurements are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius.  

	Date
	Wash. Shore
	Bradford Is.

	8/25
	20.7
	20.7

	8/26
	20.7
	20.7

	8/27
	20.7
	20.7

	8/28
	21.0
	21.0

	8/29
	21.0
	21.1

	8/30
	20.8
	20.9

	8/31
	20.6
	20.7


4.4 Sensor Calibration.  Checked calibration on 28 August this week.  

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

5. MISCELLANEOUS

5.1 B-branch and Cascade Island are in manual mode until tailwater stillwells can be installed this winter.

5.2 Turbulent flows from spillbay 18 enter the side entrance gate of Bradford Island B-branch ladder, causing poor entrance conditions.  CG funds will be used to build a bulkhead for B-branch.

5.3 During low tailwater, the PH2 monoliths are unable to maintain greater than 13’ openings.  

5.4 The digital temperature probe at the AFF appears to be out of calibration.  We cannot recalibrate it until the lab is dewatered this winter.  University of Idaho is using a thermometer to track temperatures.

5.5 As of 28 August, all fishways are in non shad passage mode.  Weir 37 still may occasionally be out of criteria because it is in manual until a still well can be installed this winter.

5.6 Main dam went on seal from 0418 until 0500 on 25 August as requested by  Skamania County Sheriff.  The outage was necessary to search for a deceased person.

5.7 On 25, 26, and 27 August , one dead adult lamprey a day was found on the DSM2 walkway, near orifice 11A-S.  We believe the lamprey were leaving the channel along the east wall, attracted by the spray from the jet out of 11A-S and landing on the grated walkway.  After consulting with the NMFS lamprey biologist, BON fisheries placed plywood over the area where the orifice jet from 11A-S sprays through the grated walkway.  Two by fours were wedged between the wall and the handrail at the south end.  No lamprey have been found since the placement of the wood barriers.  

5.8 The PDS screen cleaner failed on 26 August.  A new drive shaft has been ordered.  Until it can be replaced, the screen will have to be cleaned manually.

5.9 On 29 August, chain gate 10C was closed for PH1 crane rail work.  Per NMFS request, chain gate 6B has been opened to substitute for 10C.  We will open 6B when middle units are operating and 1B when end units are operating.

5.10 University of Idaho had a fish mortality on 29 August.  An unclipped chinook died shortly after tagging.  The fish showed no signs of pre tagging stress but did have a deep mouth wound.  Digital photos and a report were turned in to Project Fisheries.  For more information please contact Mr. Steve Lee at 509-427-7259.

5.11 Main dam on seal at 2359 on 31 August.  End of spill season.  Bays 1 and 18 will be open 6” for adult attraction during daylight hours.

 DEBORAH L. CHENOWETH

                                 

                                                             Operations Project Manager

//S//

1
3

