CENWP-OP-B                                                                                                                                  12 November 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 45 of 2002, which covers the period 03 through 09 November 2002.  

1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 116.1 to 123.2 kcfs.  Daily project tailwater elevation averaged 10.7’ to 11.8’ msl.  Daily project forebay elevation averaged 74.2’ to 76.0’ msl.  River temperature averaged 50° F.  Daily turbidity measured 6.0’ to 7.0’ on the secchi disk.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are open 6” during daylight hours.  Spill averaged. 1.8 to 2.2 kcfs.

1.3 Unit Operation

1.3.1 Unit 1 remains out of service for turbine rehab.

1.3.2 Unit 5 remains out of service for turbine rehab.

1.3.3 Unit 6 was out of service from 0500 08 November until 1818 09 November for the Bank 5/6 outage.

1.3.4 Unit 7 remains forced out of service for crane rail work.

1.3.5 Unit 8 remains forced out of service for crane rail work.

1.3.6 Unit 9 remains out of service for an overhaul.

1.3.7 Unit 10 remains forced out of service for crane rail work. 

1.3.8 Unit 11 was out of service from 1000 until 1054 on 06 November for STS repairs.

1.3.9 Unit 15 was out of service from 1100 until 1136 on 06 November for STS repairs.

1.3.10 Unit 16 remains out of service for an overhaul.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  Fish Unit 1 remains out of service for overhaul and stator rewind.

1.5 Gatewell drawdowns were measured on 06 November.

2.  ACTIVITIES. 
2.1 AWS Closures.  The following AWS closures occurred this reporting week.

FV1-1 closed for cleaning on 03 November from 0635 until 0704 and 04 November from 1515 until 1540.

FV3-9 closed for cleaning on 03 November from 0810 until 0830.

FV5-9 closed for cleaning on 03 November from 0754 until 0802 and 07 November from 1605 until 1610.

Weir 37 closed for cleaning on 03 November from 0732 until 0751.



FV6-9 closed for cleaning on 05 November from 0700 until 0705 and 07 November from 1020 until 1040.

2.2 STS/VBS Inspections.  The following STS/VBSs were inspected this reporting week. 

	Unit
	Date
	Run Hours
	Comments

	11
	11/06
	777
	STS pulled for inspection, could not view with video

	12
	11/04
	651
	

	13
	11/04
	644
	

	14
	11/05
	650
	

	15
	11/05
	660
	STS pulled for inspection, could not view with video

	17
	11/05
	694
	

	18
	11/05
	695
	


Table 1.  STS Inspection Dates.

2.3 Dewatering and Fish Salvage.   Biologists removed 44 crayfish, 69 sculpin, 1 bass, 1 sturgeon, 1 stickleback and 1 bluegill from Unit 5 tail logs on 05 November.  No fish were found on Unit 5 headgates.

3.  RESEARCH.

3.1 NMFS Lamprey.  Tracking continues.

3.2 NMFS Saltwater Rearing.  Rearing continues.  Specific data available from Lyle Gilbreath. 

3.3 PSMFC/NMFS Adult PIT.  Some detectors have developed leaks, however no repairs are scheduled for 2002/03 maintenance season.

3.4 WDFW Fish Counting.  24-hr video counts at Bradford Island and Washington Shore.

3.5 WDFW Chum tagging.  Collection and tagging of adult chum salmon started on 05 November.  

4.  FISHWAYS 
4.1 Project biologists inspected 03-09 November this week.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR/WAR

	All week
	Main dam, 

PH2
	Avian wires broken or removed
	Vandalism and BCC work. 
	Will be repaired this winter.
	

	All week
	PH1 PCC velocity
	Velocity <1.5 fps on electronic meter.
	Unknown
	No action taken.
	

	11/07-11/09
	PH2 PCC velocity
	Velocity <1.5fps on the electronic meter.
	Low TW causes an inaccurate reading.
	Sensor relocation this winter.
	

	11/06-11/09
	Weir 37
	Reading > or < 1.0’
	Weir is in manual.
	Stillwell to be installed this winter
	


4.3 Fish Ladder Temperatures.  Measurements are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius.  

	Date
	Wash. Shore
	Bradford Is.

	11/03
	11.3
	11.3

	11/04
	11.2
	11.2

	11/05
	11.3
	11.3

	11/06
	11.0
	11.0

	11/07
	10.9
	10.8

	11/08
	11.1
	11.1

	11/09
	11.2
	11.2


4.4 Sensor Calibration.  Checked calibration on 03 November this week.  

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

5. MISCELLANEOUS

5.1 B-branch and Cascade Island are in manual mode until tailwater stillwells can be installed this winter.

5.2 During low tailwater, the PH2 monoliths are unable to maintain greater than 13’ openings.  

5.3 During low tailwater, the PH1 weir gates are unable to maintain greater than 8’ openings.

5.4 A bird was removed alive from 16B gatewell slot on 03 November.

5.5 FV1-1 was out of service from 0400 on 05 November until 1345 on 07 November due to a blown motor.  While the motor was being replaced the collection channel was manually adjusted to maintain criteria.   

5.6 As of 06 November, and until further notice, the Project has a hard constraint tailwater elevation no less than 11.1’ msl during all hours and a soft constraint of 11.1’-11.5’msl between 0700-1900 hours.  This is for the protection of the chum redds around Ives Island.

5.7 Several dead salmonids were spotted upstream of the Corps’ Mt. St. Helens Sediment Retention Structure (SRS).   Project Biologists investigated and found that the clipped carcasses were part of WDFW’s nutrient enhancement program.

 JAMES R. MAHAR

                                 

                                                           Operations Manager

//S//

1
2

