CENWP-OP-B                                                                                                                                  17 November 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 46 of 2002, which covers the period 10 through 16 November 2002.  

1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 121.1 to 131.3 kcfs.  Daily project tailwater elevation averaged 11.7’ to 12.1’ msl.  Daily project forebay elevation averaged 73.5’ to 75.5’ msl.  River temperature averaged 40 to 50° F.  Daily turbidity measured 4.0’ to 7.0’ on the secchi disk.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are open 6” during daylight hours.  Spill averaged. 1.8 to 2.1 kcfs.

1.3 Unit Operation

1.3.1 Unit 1 remains out of service for turbine rehab.

1.3.2 Unit 2 was out of service for STS repair from 1000 until 1106 on 14 November.

1.3.3 Unit 5 returned to service after a 72 hour test, Kaplan oil leak repair and STS installation at 0906 on 14 November.

1.3.4 Unit 7 remains forced out of service for crane rail work.

1.3.5 Unit 8 remains forced out of service for crane rail work.

1.3.6 Unit 9 remains out of service for an overhaul.

1.3.7 Unit 10 remains forced out of service for crane rail work. 

1.3.8 Unit 16 remains out of service for an overhaul.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  Fish Unit 1 remains out of service for overhaul and stator rewind.

1.5 Gatewell drawdowns were measured on 13 November.

2.  ACTIVITIES. 
2.1 AWS Closures.  No AWS closures occurred this reporting week.

2.2 STS/VBS Inspections.  The following STS/VBSs were inspected this reporting week. 

	Unit
	Date
	Run Hours
	Comments

	2
	11/14
	1302
	Crane rail contract work prevented earlier inspection

	3
	11/14
	819
	Crane rail contract work prevented earlier inspection

	4
	11/14
	388
	

	5
	11/13
	
	Out of service

	6
	11/13
	176
	

	8
	11/12
	
	8A ESBS was shut down.  The cleaner is not working properly.


Table 1.  STS Inspection Dates.

2.3 Dewatering and Fish Salvage.   No dewatering or fish salvage activities this reporting week.

3.  RESEARCH.

3.1 NMFS Lamprey.  Tracking continues.

3.2 NMFS Saltwater Rearing.  Rearing continues.  Specific data available from Lyle Gilbreath. 

3.3 PSMFC/NMFS Adult PIT.  Some detectors have developed leaks, however no repairs are scheduled for 2002/03 maintenance season.

3.4 WDFW Fish Counting.  24-hr video counts at Bradford Island and Washington Shore.

3.5 WDFW Chum tagging.  Collection and tagging of adult chum salmon continues.  

4.  FISHWAYS 
4.1 Project biologists inspected 10-16 November this week.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR/WAR

	All week
	Main dam, 

PH2
	Avian wires broken or removed
	Vandalism and BCC work. 
	Will be repaired this winter.
	

	All week
	PH1 PCC velocity
	Velocity <1.5 fps on electronic meter.
	Unknown
	No action taken.
	

	All week
	PH2 PCC velocity
	Velocity <1.5fps on the electronic meter.
	Low TW causes an inaccurate reading.
	Sensor relocation this winter.
	

	11/11, 11/13
	Weir 37
	Reading > or < 1.0’
	Weir is in manual.
	Stillwell to be installed this winter
	

	11/14
	Bradford Island
	A and B branch staff gauges
	Unknown
	Trashracks cleaned, operators to adjust FV3-9
	


4.3 Fish Ladder Temperatures.  Measurements are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius.  

	Date
	Wash. Shore
	Bradford Is.

	11/10
	11.0
	11.0

	11/11
	10.9
	10.9

	11/12
	10.8
	10.8

	11/13
	10.8
	10.8

	11/14
	10.8
	10.8

	11/15
	10.5
	10.5

	11/16
	10.1
	10.1


4.4 Sensor Calibration.  Checked calibration on 10 and 14 November this week.  

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

5. MISCELLANEOUS

5.1 B-branch and Cascade Island are in manual mode until tailwater stillwells can be installed this winter.

5.2 During low tailwater, the PH2 monoliths are unable to maintain greater than 13’ openings.  

5.3 During low tailwater, the PH1 weir gates are unable to maintain greater than 8’ openings.

5.4 As of 13 November, and until further notice, the Project has a hard constraint tailwater elevation no less than 11.3’ msl during all hours and a soft constraint of 11.3’-11.7’ msl between 0700-1900 hours.  This is for the protection of the chum redds around Ives Island.

5.5 On 13 November, Unit 8A ESBS cleaner failed to function properly.  Until the screen can be pulled, it is out of service.  8B and 8C are still in operation.

5.6 The South Monolith at Washington Shore went out of service at 0530 on 15 November.  This is to facilitate B2 Corner Collector construction on Cascade Island.

5.7 PH1 became the priority powerhouse at 0542 on 15 November.

 JAMES R. MAHAR

                                 

                                                           Operations Manager

//S//

1
2

