CENWP-OP-B                                                                                                                                  02 December 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 48 of 2002, which covers the period 24 through 30 November 2002.  

1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 126.3 to 143.6 kcfs.  Daily project tailwater elevation averaged 11.5’ to 12.3’ msl.  Daily project forebay elevation averaged 73.3’ to 75.5’ msl.  River temperature averaged 46 to 49° F.  Daily turbidity measured 5.0’ to 7.0’ on the secchi disk.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are open 6” during daylight hours.  Spill averaged 1.8 to 1.9 kcfs.

1.3 Unit Operation

1.3.1 Unit 1 remains out of service for turbine rehab.

1.3.2 Unit 2 was out of service from 1018 until 1024 on 25 November because bank 1/ 2 was tripped.

1.3.3 Unit 7 remains forced out of service for crane rail work.

1.3.4 Unit 8 remains forced out of service for crane rail work.

1.3.5 Unit 9 remains out of service for an overhaul.

1.3.6 Unit 10 remains forced out of service for crane rail work. 

1.3.7 Units 11 and 12 were out of service for B2 corner collector dive operations from about 0600 until 1730 on 25-27 November.

1.3.8 Unit 16 remains out of service for an overhaul.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  Fish Unit 1 remains out of service for overhaul and stator rewind.

1.5 Gatewell drawdowns were measured on 27 November.

2.  ACTIVITIES. 
2.1 AWS Closures.  The following AWS valves were closed for cleaning.

27 November- FV1-1 from 1320 until 1345

29 November- FV1-1 from 0810 until 0840, from 1210 until 1324, from 1845 until 0525 on 30 November.





 FV3-7 from 1340 until 1350





 FV3-9 from 1340 until 1350





 FV 5-9 from 1350 until 1415





 FV6-9 from 1430 until 1500





 Washington Shore exit from 1430 until 1500.

2.2 STS/VBS Inspections.  No STS/VBSs were inspected this reporting week. 

2.3 Dewatering and Fish Salvage.  WDFW and PSMFC biologists assisted with the AFF dewatering on 25 November.  Fifteen coho, ten steelhead, two shad, two suckers, and seven whitefish were released back to the Washington Shore ladder, one steelhead was released upstream of the navlock.

3.  RESEARCH.

3.1 NMFS Lamprey.  Tracking continues.

3.2 NMFS Saltwater Rearing.  Rearing continues.  Specific data available from Lyle Gilbreath. 

3.3 WDFW Fish Counting.  24-hr video counts at Bradford Island and Washington Shore.

4.  FISHWAYS 
4.1 Project biologists inspected 24-30 November this week.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR/WAR

	All week
	Main dam, 

PH2
	Avian wires broken or removed
	Vandalism and BCC work. 
	Will be repaired this winter.
	

	11/24, 11/26-30
	PH1 PCC velocity
	Velocity <1.5 fps on electronic meter.
	Unknown
	No action taken.
	

	All week
	PH2 PCC velocity
	Velocity <1.5fps on the electronic meter.
	Low TW causes an inaccurate reading.
	Sensor relocation this winter.
	

	All week
	North monolith
	NDE differential <1.0’
	F1 OOS
	Operators to adjust gates.
	


4.3 Fish Ladder Temperatures.  Measurements are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius.  

	Date
	Wash. Shore
	Bradford Is.

	11/24
	10.4
	10.4

	11/25
	10.1
	10.2

	11/26
	9.8
	9.8

	11/27
	9.5
	9.5

	11/28
	9.3
	9.3

	11/29
	9.0
	9.0

	11/30
	8.8
	8.9


4.4 Sensor Calibration.  Calibration checked on 27 November this week.  

4.5 Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

5. MISCELLANEOUS

5.1 B-branch and Cascade Island are in manual mode until tailwater stillwells can be installed this winter.

5.2 During low tailwater, the PH2 monoliths are unable to maintain greater than 13’ openings.  

5.3 During low tailwater, the PH1 weir gates are unable to maintain greater than 8’ openings.

5.4 As of 13 November, and until further notice, the Project has a hard constraint tailwater elevation no less than 11.3’ msl during all hours and a soft constraint of 11.3’-11.7’msl between 0700-1900 hours.  This is for the protection of the chum redds around Ives Island.

5.5 On 13 November, Unit 8A ESBS cleaner failed to function properly.  Until the screen can be pulled, it is out of service.  8B and 8C are still in operation.

5.6 Several dead juvenile shad were found mixed in with aquatic vegetation on the DSM2 screen cleaner brushes.  The juveniles appeared to have sustained traumatic injuries.  No action will be taken at this time, but we mention it as a possible explanation for the increased juvenile mortality we’ve seen in the spring.  An airburst system will be installed in 2003/04 winter maintenance season.

5.7 FV6-9 has a new transducer.  It seems to be controlling properly in auto at this time.

 JAMES R. MAHAR

                                 

                                                           Operations Manager

//S//

1
2

