CENWP-OP-B                                                                                                                                           22 June 2003

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 25 of 2003, which covers the period 15 through 21 June 2003.

1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 198.4 to 281.8 kcfs.  Daily project tailwater elevation averaged 15.5’ to 20.5’ msl.  Daily project forebay elevation averaged 73.9’ to 75.5’ msl.  River temperature averaged 60 to 61° F.  Daily turbidity measured 3.0’ to 5.5’ on the secchi disk.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascade Island and Bradford Island fishways respectively, are included in the spill pattern.  Spill averaged 92.9 to 154.3 kcfs.  

1.3 Unit Operation

1.3.1 Unit 1 remains out of service for turbine rehab.

1.3.2 Unit 8 was out of service from 0718 until 0912 on 16 June for brush replacement/repair and from 1142 until 1542 on 16 June for ESBS repairs.

1.3.3 Unit 13 was out of service from 0724 until 0912 on 16 June and from 0712 until 0924 on 19 June for gap loss study equipment install/removal.

1.3.4 Unit 15 remains out of service due to a broken restoring cable.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.   

1.5 Gatewell drawdowns are measured on Wednesdays.

2.  ACTIVITIES. 
2.1 AWS Closures.  The following AWS valves were closed for cleaning this reporting week.

2.1.1 FV1-1 from 1340 until 1355 on 19 June.

2.1.2 FV3-7 from 1320 until 1340 on 19 June.

2.2 STS/VBS Inspections.  No STS/VBS inspections were conducted this reporting week.

2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage activities this reporting week.

3.  RESEARCH.

3.1 CRITFC.  Sampling of chinook, sockeye, and coho continues until 31 October.

3.2 NMFS Lamprey.  Trapping, tagging and tracking continue.

3.3 OCFWRU.  Fish collection continues. 

3.4 ODFW Steelhead.  Trapping continues. 

3.5 PSMFC at DSM1.  Continuous PIT tag interrogation continues.  GBT and monitoring continue.

3.6 PSMFC at the SMF.  SMF personnel observed 56 steelhead, 22 salmon and 354 smolts slide over the separator bars.

3.7 University of Idaho.  Adult tracking tagging and tracking continue.  

3.8 U of I Transportation Study.  Evaluation of river run vs. barged Snake River juveniles to occur May-June.  

3.9 University of Washington.  Northern pikeminnow tagging and tracking from May through July.  

3.10 USGS Lamprey.  Collected 36 lamprey from NMFS on 13 June, 174 on 19 June and 20 on 20 June.

3.11 Warm Springs Tribes.  Collected 43 lamprey from NMFS on 13 June and 60 on 19 June.

3.12 WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

3.13 WES/Battelle/BAE systems Juvenile hydroacoustic monitoring.  Gap loss monitoring continues in Unit 13.  Will move to Unit 17 on 23 June.

4.  FISHWAYS 
4.1 Project biologists inspected 15 through 22 June this week. 

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR/WAR

	6/15-18, 6/21
	PH1 PCC
	Velocity <1.5fps
	Meter in slowest part of channel
	No response at this time.
	

	All week
	PH2 PCC
	No velocity measure.
	Meter is missing
	See misc. 5.1
	

	6/15-18
	Weir 37 
	Reading >or <1.3’ +/- .1’
	Believed to be shad related.
	
	

	6/15
	Weir 38
	Reading >or <1.3’ +/- .1’
	
	Adjusted Valve #2
	

	6/15, 17
	UMT weir
	Reading >or <1.3’ +/- .1’
	Unknown
	FV5-9 adjusted see misc. 5.3
	


4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Kelvin.  http://students.washington.edu/kyle/temptable.jpg 

	Date
	Wash. Shore
	Bradford Is.
	AFF exit

	6/15
	289.9
	289.9
	289.9

	6/16
	290.0
	290.2
	290.0

	6/17
	290.3
	290.4
	290.2

	6/18
	290.4
	290.4
	290.3

	6/19
	290.3
	290.2
	290.2

	6/20
	289.9
	289.9
	289.9

	6/21
	289.9
	289.7
	289.7


4.4 Sensor Calibration.  Calibration was checked on 15 June this reporting week.

4.5  Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

5. MISCELLANEOUS

5.1 Divers discovered the PH2 velocity meter was missing from the collection channel.  A new meter will be installed during the mid season dives this summer.

5.2 As of 1500 on 30 May, the Project is restricted to a maximum tailwater of 27’.  This is to prevent overtopping the bulkhead in the B2 Corner Collector.  The bulkhead went in about a month ago and is located at Station 24 +56 (near the start of the monolith).  

5.3 FV5-9 was in manual from 1150 until 1250 on 15 June due to the valve not controlling properly.

5.4 From 0525 until 0845 on 18 June Bay 6 was stuck at 3.5’.  Bays 3, 4, 5, 7 and 9 were all lowered 1’ to compensate for Bay 6.  Bay 6 can now be controlled by GDACS.

JAMES R. MAHAR, P.E.

Operations Manager

//S//

1
2

