CENWP-OP-B                                                                                                                        10 August 2003

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 32 of 2003, which covers the period 03 through 09 August 2003. 

1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 134.1 to 152.1 kcfs.  Daily project tailwater elevation averaged 11.0’ to 11.7’ msl.  Daily project forebay elevation averaged 74.5’ to 75.2’ msl.  River temperature averaged 69 to 70° F.  Daily turbidity measured 4.0’ to 7.0’ on the secchi disk.

1.2 Spill Bays 1 and 18, which supply attraction flow for Cascade Island and Bradford Island fishways respectively, are included in the spill pattern.  Spill averaged 85.1 to 88.1 kcfs.  

1.3 Unit Operation

1.3.1 Unit 1 remains out of service for turbine rehab.

1.3.2 Unit 2 went out of service at 0718 on 06 August due to crane rail replacement.  See const. 5.2
1.3.3 Unit 3 went out of service at 0718 on 06 August due to crane rail replacement.  See const. 5.2
1.3.4 Unit 4 went out of service at 0718 on 06 August due to crane rail replacement. See const. 5.2
1.3.5 Unit 5 went out of service at 1848 on 03 August for a bank 5/6, line 2 outage.  Unit 5 remains out of service due to crane rail replacement.  See const. 5.2
1.3.6 Unit 6 went out of service at 1848 on 03 August for a bank 5/6, line 2 outage.  Unit 6 remains out of service due to crane rail replacement.  See const. 5.2
1.3.7 Unit 7 remains out of service for its five year overhaul.

1.3.8 Unit 8 went out of service at 1848 on 03 August for a bank 5/6, line 2 outage.  Unit 8 remains out of service due to crane rail replacement.  See const. 5.2
1.3.9 Unit 13 was out of service from 0730 until 0925 on 04 August for gap loss test equipment removal from the STS.

1.3.10 Unit 14 remains out of service for its five year overhaul.

1.3.11 Unit 15 was out of service from 1700 on 04 August until 0825 on 05 August due to a problem with the governor power supply.

1.3.12 Unit 17 was out of service from 2254 on 03 August until 1000 on 06 August for governor calibration.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  

1.5 Gatewell drawdowns are measured on Wednesdays.

2.  ACTIVITIES. 
2.1 AWS Closures.  No AWS valves were closed this reporting week.

2.2 STS/VBS Inspections.  No STS/VBS inspections were conducted this reporting week.

2.3 Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this week.  

3.  RESEARCH.

3.1 CRITFC.  Sampling has concluded until water levels drop below 70º F.

3.2 NMFS Lamprey.  Trapping, tagging and tracking continue.  See misc. 6.4
3.3 ODFW Steelhead.  Trapping continues.  See misc. 6.4
3.4 PSMFC at DSM1.  All PIT tag interrogation and monitoring concluded at 0800 on 31 July.

3.5 PSMFC at the SMF.  GBT exams continue.  One unknown salmonid slid over the separator bars.

3.6 University of Idaho.  Adult tracking tagging and tracking continue.  See misc. 6.4
3.7 U of I Transportation Study.  Study concluded as of 08 August.  

3.8 WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

3.9 WDFW Tule counter.  Visual counts start at both ladders on 15 August.

4.  FISHWAYS 
4.1 Project biologists inspected 03 through 09 August this reporting week.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR/WAR

	All week
	PH1 PCC
	Velocity <1.5fps
	Meter in slowest part of channel
	No response at this time.
	

	All week
	PH2 PCC
	No velocity measure.
	Cable not installed.
	See misc. 6.1
	

	8/7
	Weir 37/38
	Reading < or > 1.3’
	Unknown
	No response at this time.
	

	All week
	PH1 ITS
	Chain gate 7A and ITS end gate closed.
	Crane rail work
	8B opened.  See const. 5.2.1
	


4.3 Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Kelvin.  http://students.washington.edu/kyle/temptable.jpg   (295.37K = 22.22C= 72F)

	Date
	WA Shore
	Bradford Is.
	AFF exit

	8/03
	295.0
	294.9
	295.0

	8/04
	294.9
	295.0
	294.9

	8/05
	295.0
	294.9
	295.1

	8/06
	295.0
	295.0
	295.0

	8/07
	295.2
	295.1
	295.2

	8/08
	295.4
	295.2
	295.4

	8/09
	295.4
	295.4
	295.5


4.4 Sensor Calibration.  Calibration was checked on 05 and 08 August this reporting week.

4.5  Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

5. CONSTRUCTION

5.1 PH 2 Corner Collector

5.1.1 In a 10 July teletype the Project was given a hard constraint maximum tailwater of 16’ until 01 September.  This is for the B2CC work at PH2.  In a 15 July teletype, the maximum tailwater constraint overrules spill to the 120% gas cap if spill raises tailwater over 16’.

5.2 PH 1 Crane Rail Replacement- started on 01 August and will continue until 16 December.
5.2.1 Chain gate 7A was closed on 31 July so contractors could install their scaffolding, 8A has been opened to compensate.  As a safety precaution, the end gate will be closed during the hours the contractors are working over the ITS.  The end gate will be opened each evening to flush fish.  USACE made a determination of “no effect” on 01 August.

5.2.2 On 04 August, the Project needed to run units as PH1 due to a lack of available units at PH2.  Unit 4 was in service from 1454 until 1912 and Unit 3 from 1806 until 1912.  At 1912, operators shutdown units 3 and 4, since the STSs are installed, and started units 9 and 10, following FPP guidelines for turbine operations for screened units.  Units 9 and 10 were in service from 1912 until 2130.   

5.2.3 Due to fish passage concerns, regional coordination resulted in an agreement on 08 August to pull screens from Units 9 and 10 until 15 September.  Further, if units 9 or 10 are run then the contractors will be notified and the end gate opened as soon as they have cleared the area.  

5.2.4 PH1 ITS was closed from approximately 0500 until 1700 from 04- 09 August.   Two notable exceptions are on 06 August when it wasn’t opened until 1925 and on 09 August when it was opened at 1030 due to the contractor having difficulty with the saw.

6. MISCELLANEOUS

6.1 A new velocity meter was installed for PH2 PCC during the mid season dive on 21 July.  We are now waiting for the electricians to finish installation.

6.2 As of 28 June, the Project will have a daytime spill of 75 kcfs.

6.3 F2 north orifices were opened from 0748 on 04 August until 2100 on 07 August to help maintain water levels in DSM2.

6.4 Water temperatures remain near 72ºF this reporting week.  Researchers trapped early in the week, closing the AFF down before noon.  They will be allowed back in next week for one day if temperatures remain at or above 72ºF or four days a week if temperatures are between 70ºF and 72ºF.

JAMES R. MAHAR, P.E.

Operations Manager

//S//

1
3

