CENWP-OP-B                                                                                                                        09 February 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 06 of 2004, which covers the period 01 through 07 February 2004.

1.  OPERATION SUMMARY.

1.1 Daily river flow averaged 132.7 to 172.4 kcfs.  Daily project tailwater elevation averaged 14.1’ to 16.1’ msl.  Daily project forebay elevation averaged 74.2’ to 76.3’ msl.  River temperature averaged 37 to 38° F.  Daily turbidity measured 3.0 to 5.5 on the secchi disk.  

1.2 Spill Bays 1 and 18 will remain closed until more fish start passing the Project or spill season starts.  Spill averaged 0 kcfs.  

1.3 Unit operation

1.3.1 Unit 0 was out of service from 0355 until 1720 on 02 February and from 0441 until 1411 on 03 February for PSC removal.

1.3.2 Unit 1 remains out of service for turbine rehab.

1.3.3 Unit 2 was out of service from 0400- 1647 on 02 Feb., 0441- 1715 on 03 Feb., 0357- 1657 on 04 Feb., 0506- 1701 on 05 Feb., and 0420- 1343 on 06 Feb. for PSC removal.

1.3.4 Unit 3 was out of service from 1400- 1715 on 03 Feb., 0357- 1657 on 04 Feb., 0506- 1701 on 05 Feb., and 0420- 1343 on 06 Feb. for PSC removal.

1.3.5 Unit 4 was out of service from 1155 until 1701 on 05 February and from 0420 until 1343 on 06 February for PSC removal.

1.3.6 Unit 10 went out of service at 1411 on 05 February due to an upper guide bearing problem.

1.3.7 Unit 11 remains out of service. 

1.3.8 Unit 12 was out of service from 0845 until 1643 on 04 February and from 0654 until 0837 on 05 February for transducer installation.

1.3.9 Unit 13 was out of service from 0842 until 1243 on 05 February for transducer installation.

1.3.10 Unit 14 was out of service from 1249 until 1513 on 05 February for transducer installation.

1.3.11 Unit 15 was out of service from 0745 until 1202 on 06 February for transducer installation.

1.3.12 Unit 16 was out of service from 0817 until 1126 on 07 February for transducer installation.

1.3.13 Unit 17 remains out of service for VBS modifications.

1.3.14 Unit 18 was out of service from 2030 on 05 February until 0120 on 06 February and from 1751 on 06 February until 0212 on 07 February to facilitate dredging in front of the fish units.

1.4 Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  

1.4.1 F1 was out of service from 2030 on 05 February until 0124 on 06 February and from 1732 on 06 February until 0218 on 07 February due to dredging operations for the new Fish Unit trashracks and trash rake.

1.4.2 F2 remains out of service for winter maintenance.

1.5 Gatewell drawdowns are measured on Wednesdays.

2.  ACTIVITIES. 
2.1 AWS Closures. The following AWS valves were closed this reporting week.

FV1-1—remains closed.

FV3-7— remains closed.

FV3-9— remains closed.

FV4-3/FV4-4— remains closed.

2.2 STS/VBS Inspections.  All STSs are removed until fish passage season.

2.3 Dewatering and Fish Salvage.  The following dewatering or salvage activities this reporting week. 

2.3.1 Project Fisheries walked the B2CC on 06 February after the gate test.  No fish or debris were found in the channel.

3.  RESEARCH.

3.1 Battelle FGE testing.  Transducers installed at PH2.

3.2 USGS FPE testing.  Radio telemetry equipment to be installed on the Project throughout February.  

3.3 WDFW Fish Counting.  16-hr video counts at Washington Shore.

4.  FISHWAYS 
4.1 Project biologists inspected 02, 04, 05 February this reporting week.

4.2 Fish Passage Plan Observations.

	DATE
	LOCATion
	FPP Deviation
	CAUSE
	RESPONSE
	TR#

	All week
	PH2 PCC
	Velocity <1.5fps
	Unknown
	Electricians to look at.
	


4.3 Fish Ladder Temperatures.  Temperatures are not recorded during winter maintenance season.

4.4 Sensor Calibration.  Calibration was checked on 05 February.

4.5  Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week. 

4.6 Fishway Status.  

4.6.1 Both DSMs remain out of service.

4.6.2 Bradford Island fishway remains dewatered.  

4.6.3 The south end of PH1 PCC will be dewatered on 09 February.  This is for hydraulic engineers to look at the AWS and the ladder.

5 CONSTRUCTION

5.1 PH 2 Corner Collector- The corner collector was opened from 1025 until 1251 on 06 February for the gate test and for hydraulic testing.  Hydraulic tests to be conducted 18-20 February.

5.2 PH 2 Corner Collector Hi-Q PIT tag detector- Prototype still planned for installation in 2004.

5.3 PH2 Corner Collector Avian Wires- Avian wire installation scheduled for 25 February over the plunge pool.   

5.4 PH1 PSC Removal.  Removal completed.

5.5 Unit 17 VBS mods.  Modifications underway.

5.6 B2 Follow-on.  The contractors are still working on the airburst system in DSM2.  Their schedule has been extended by 3.5 days.  A pipe survey completed on 03 and 04 February.  

5.7 Fish Unit Trashracks.  Dredging of the forebay occurred on 05-06 February.  Divers are scheduled to install blocked panel trashracks 23-25 February.  The trashrake will arrive this Spring.

6 MISCELLANEOUS

6.1 Per a teletype sent on 18 December, Project tailwater will have a hard constraint of 11.8’ and a soft constraint of 11.8’ to 12.1’ between the hours of 0700 until 1700.  This constraint is for chum spawning habitat located below the dam.  

6.2 BPA requested a 1% violation from 1752 until 1806 on 06 February.

JAMES R. MAHAR, P.E.

Operations Manager

//S//

1
2

